## General
JalTantra: System For Optimization of Piped Water Networks
developed by CSE and CTARA departments of IIT Bombay
Feb 07, 2017 20:50 PM
Network Name |  |  | Sample
Minimum Node Pressure |  |  | 7
Default Pipe Roughness 'C' |  |  | 140
Minimum Headloss per KM |  |  | 0
Maximum Headloss per KM |  |  | 10
Maximum Water Speed |  |  | 1.5
Maximum Pipe Pressure
Number of Supply Hours |  |  | 12
Source Node ID |  |  | 8
Source Node Name |  |  | Node8
Source Elevation |  |  | 505
Source Head |  |  | 530
Number of Nodes |  |  | 10
ESR Enabled |  |  | TRUE
Secondary Supply Hours |  |  | 6
ESR Capacity Factor |  |  | 0.5
Maximum ESR Height |  |  | 25
Allow ESRs at zero demand nodes |  |  | TRUE
Nodes that must have ESRs
Nodes that must not have ESRs |  |  | 4;7
Pump Enabled |  |  | TRUE
Minimum Pump Size |  |  | 1
Pump Efficiency |  |  | 70
Capital Cost per kW |  |  | 30000
Energy Cost per kWh |  |  | 6.5
Design Lifetime |  |  | 15
Discount Rate |  |  | 7
Inflation Rate |  |  | 5
Pipes that must not have Pumps |  |  | 10
Total Length of Network |  |  | 35735
Total Length of New Pipes |  |  | 28390
Total Pipe Cost |  |  | 13800517.827
Total ESR Cost |  |  | 4855836
Total Pump Cost |  |  | 2487508.4074
Total Cost |  |  | 21143862.2343
NODE RESULTS
Node ID | Node Name | Demand | Elevation | Head | Pressure | Min. Pressure
1 | Node1 | 8.4 | 442 | 449 | 7 | 7
2 | Node2 | 1.6 | 477 | 491.1644 | 14.1644 | 7
3 | Node3 | 6.8 | 496 | 518.6377 | 22.6377 | 7
4 | Node4 | 7 | 464 | 480.9656 | 16.9656 | 7
6 | Node6 | 7.2 | 390 | 424.345 | 34.345 | 7
7 | Node7 | 10.4 | 493 | 500 | 7 | 7
9 | Node9 | 0 | 517 | 524.6102 | 7.6102 | 7
10 | Node10 | 0 | 509 | 516 | 7 | 7
11 | Node11 | 0 | 472 | 479 | 7 | 7
PIPE RESULTS
Pipe ID | Start Node | End Node | Length | Flow | Speed | Diameter | Roughness 'C' | Headloss | Headloss per KM | Cost | Pump Head | Pump Power | Valve Setting | Status
2 | 3 | 7 | 7345 | 8.4488 | 0.88904 | 110 | 140 | 56.0761 | 7.6346 | 0 | 44.4384 | 6.4746
|  |  | 7345 | 1.9512 | 0.62593 | 63 | 140 | 56.0761 | 7.6346 | 852020 | 44.4384 | 6.4746 |  | Parallel
3 | 2 | 6 | 3491 | 7.2 | 0.75763 | 110 | 140 | 19.8193 | 5.6773 | 1186940 |  |  | 40
4 | 2 | 4 | 2442 | 15.4 | 1.0004 | 140 | 140 | 17.5119 | 7.1711 | 1406592 | 14.3131 | 3.088
5 | 9 | 3 | 1943 | 24.9 | 0.79259 | 200 | 140 | 5.9726 | 3.0739 | 2162559
6 | 8 | 9 | 2686 | 24.9 | 0.79259 | 200 | 140 | 8.2564 | 3.0739 | 2989518 | 2.8667 | 1
7 | 10 | 2 | 4808 | 12.9 | 0.838 | 140 | 140 | 24.8356 | 5.1655 | 2769408
8 | 3 | 10 | 59.4162 | 12.9 | 0.838 | 140 | 140 | 0.30691 | 5.1655 | 34223.76
8 | 3 | 10 | 864.5838 | 12.9 | 0.64159 | 160 | 140 | 2.3308 | 2.6958 | 648437.8125
9 | 11 | 1 | 3631.3367 | 8.4 | 0.8839 | 110 | 140 | 27.4278 | 7.5531 | 1234654.4916
9 | 11 | 1 | 634.6633 | 8.4 | 0.68449 | 125 | 140 | 2.5722 | 4.0528 | 292579.7629
10 | 4 | 11 | 485 | 8.4 | 0.68449 | 125 | 140 | 1.9656 | 4.0528 | 223585
COST RESULTS OF NEW PIPES
Diameter | Length | Cost | Cumulative Cost
63 | 7345 | 852020 | 852020
110 | 7122.3367 | 2421594.4916 | 3273614.4916
125 | 1119.6633 | 516164.7629 | 3789779.2545
140 | 7309.4163 | 4210223.76 | 8000003.0145
160 | 864.5838 | 648437.8125 | 8648440.827
200 | 4629 | 5152077 | 13800517.827
Total | 28390 | 13800517.827
COST RESULTS OF ESRS
ESR Node ID | ESR Child ID | Node Name | Elevation (m) | Capacity (l) | ESR Height (m) | Cost (Rs) | Cumulative Cost (Rs)
2 |  | Node2 | 477 | 278640 | 7.1644 | 2480406 | 2480406
| 1 | Node1 | 442 | 90720
| 2 | Node2 | 477 | 34560
| 4 | Node4 | 464 | 75600
| 6 | Node6 | 390 | 77760
3 |  | Node3 | 496 | 259200 | 15.6377 | 2375430 | 4855836
| 3 | Node3 | 496 | 146880
| 7 | Node7 | 493 | 112320
COST RESULTS OF PUMPS
Pipe ID | Pump Head (m) | Pump Power (kW) | Energy Cost (Rs) | Capital Cost (Rs) | Total Cost (Rs)
2 | 44.4384 | 6.4746 | 1215468.7401 | 194238.6 | 1409707.3401
4 | 14.3131 | 3.088 | 579704.6729 | 92640 | 672344.6729
6 | 2.8667 | 1 | 375456.3944 | 30000 | 405456.3944