## General
JalTantra: System For Optimization of Piped Water Networks
developed by CSE and CTARA departments of IIT Bombay
Sep 21, 2016 15:52 PM
Network Name |  |  | Sample
Minimum Node Pressure |  |  | 7
Default Pipe Roughness 'C' |  |  | 140
Minimum Headloss per KM |  |  | 0
Maximum Headloss per KM |  |  | 10
Maximum Water Speed |  |  | 1.5
Maximum Pipe Pressure
Number of Supply Hours |  |  | 12
Source Node ID |  |  | 8
Source Node Name |  |  | Node8
Source Elevation |  |  | 505
Source Head |  |  | 530
Number of Nodes |  |  | 10
ESR Enabled |  |  | TRUE
Secondary Supply Hours |  |  | 6
ESR Capacity Factor |  |  | 0.5
Maximum ESR Height |  |  | 25
Allow ESRs at zero demand nodes |  |  | TRUE
Nodes that must have ESRs
Nodes that must not have ESRs |  |  | 4;7
Total Length of Network |  |  | 35735
Total Length of New Pipes |  |  | 28390
Total Pipe Cost |  |  | 18686861.9733
Total ESR Cost |  |  | 4855836
Total Cost |  |  | 23542697.9733
NODE RESULTS
Node ID | Node Name | Demand | Elevation | Head | Pressure | Min. Pressure
1 | Node1 | 8.4 | 442 | 449 | 7 | 7
2 | Node2 | 1.6 | 477 | 496.2712 | 19.2712 | 7
3 | Node3 | 6.8 | 496 | 518.5768 | 22.5768 | 7
4 | Node4 | 7 | 464 | 480.1319 | 16.1319 | 7
6 | Node6 | 7.2 | 390 | 469.4518 | 79.4518 | 7
7 | Node7 | 10.4 | 493 | 500 | 7 | 7
9 | Node9 | 0 | 517 | 524 | 7 | 7
10 | Node10 | 0 | 509 | 516 | 7 | 7
11 | Node11 | 0 | 472 | 479 | 7 | 7
PIPE RESULTS
Pipe ID | Start Node | End Node | Flow | Diameter | Length | Headloss | Headloss per KM | Speed | Roughness 'C' | Cost | Status
2 | 3 | 7 | 3.6043 | 110 | 7345 | 11.5768 | 1.5761 | 0.37927 | 140 | 0
|  |  | 6.7957 | 140 | 7345 | 11.5768 | 1.5761 | 0.44146 | 140 | 4230720 | Parallel
3 | 2 | 6 | 7.2 | 110 | 3491 | 19.8193 | 5.6773 | 0.75763 | 140 | 1186940
4 | 2 | 4 | 15.4 | 160 | 2442 | 9.1393 | 3.7425 | 0.76593 | 140 | 1831500
5 | 9 | 3 | 24.9 | 200 | 1533.6144 | 4.7142 | 3.0739 | 0.79259 | 140 | 1706912.8606
5 | 9 | 3 | 24.9 | 225 | 409.3856 | 0.7091 | 1.7321 | 0.62625 | 140 | 585421.3651
6 | 8 | 9 | 24.9 | 200 | 1004.3129 | 3.0871 | 3.0739 | 0.79259 | 140 | 1117800.28
6 | 8 | 9 | 24.9 | 225 | 1681.6871 | 2.9129 | 1.7321 | 0.62625 | 140 | 2404812.5244
7 | 10 | 2 | 12.9 | 140 | 2740.1897 | 14.1544 | 5.1655 | 0.838 | 140 | 1578349.2614
7 | 10 | 2 | 12.9 | 160 | 2067.8103 | 5.5744 | 2.6958 | 0.64159 | 140 | 1550857.7325
8 | 3 | 10 | 12.9 | 140 | 34.7489 | 0.17949 | 5.1655 | 0.838 | 140 | 20015.3549
8 | 3 | 10 | 12.9 | 160 | 889.2511 | 2.3973 | 2.6958 | 0.64159 | 140 | 666938.34
9 | 11 | 1 | 8.4 | 110 | 3631.3367 | 27.4278 | 7.5531 | 0.8839 | 140 | 1234654.4916
9 | 11 | 1 | 8.4 | 125 | 634.6633 | 2.5722 | 4.0528 | 0.68449 | 140 | 292579.7629
10 | 4 | 11 | 8.4 | 140 | 485 | 1.1319 | 2.3338 | 0.54567 | 140 | 279360
COST RESULTS OF NEW PIPES
Diameter | Length | Cost | Cumulative Cost
110 | 7122.3367 | 2421594.4916 | 2421594.4916
125 | 634.6633 | 292579.7629 | 2714174.2545
140 | 10604.9386 | 6108444.6163 | 8822618.8708
160 | 5399.0614 | 4049296.0725 | 12871914.9433
200 | 2537.9273 | 2824713.1406 | 15696628.0838
225 | 2091.0727 | 2990233.8895 | 18686861.9733
Total | 28390 | 18686861.9733
COST RESULTS OF ESRS
ESR Node ID | ESR Child ID | Node Name | Elevation (m) | Capacity (l) | ESR Height (m) | Cost (Rs) | Cumulative Cost (Rs)
2 |  | Node2 | 477 | 278640 | 12.2712 | 2480406 | 2480406
| 1 | Node1 | 442 | 90720
| 2 | Node2 | 477 | 34560
| 4 | Node4 | 464 | 75600
| 6 | Node6 | 390 | 77760
3 |  | Node3 | 496 | 259200 | 15.5768 | 2375430 | 4855836
| 3 | Node3 | 496 | 146880
| 7 | Node7 | 493 | 112320