CENTER FOR TECHNOLOGY ALTERNATIVES FOR RURAL AREAS

INDIAN INSTITUTE OF TECHNOLOGY, BOMBAY

Piped Water Supply System for North Karjat

Techno-Economic Feasibility Study

By

Abhishek Kumar Sinha (07D04025), Vikram Vijay (07D04014), Janhvi Doshi

Guide: Prof. Milind Sohoni

Supported by:

Dean (R&D) IITB, Mr. Ashok Jangle (Disha Kendra), Mr. Ashok Ghule and Mr. Y. P. Nivdange (MJP Karjat), Mr. Ade (Office of Minor Irrigation, Karjat)

August 2010

Abstract

Over a hundred villages in north Karjat, Raigarh district, Maharashtra, suffer from severe water shortage in the months preceding the monsoons. A few check dams have been built to alleviate the problem in some of the villages but most habitations face empty wells and defunct hand-pumps in the summer. This project aims to evaluate the techno-economic feasibility of piped water supply to this region as well to establish a universally applicable design methodology for rural piped water supply systems. The target area within the Karjat block spans 120 sq. km and has a forecasted 2041 population of over 81,000. The source is taken to be the Pej River, south of the target region. We have designed primary and secondary grids for two supply norms: a livelihood norm of 200 lpcd and a sustenance norm of 40 lpcd. Given existing design norms, engineering practices, and schedules of costs our finding is that it economically viable to supply water in pipes from Pej River to the target area at the desirable livelihood norm of 200 lpcd. We estimate the investment cost of this supply system to be around Rs. 7000 per capita at 200 lpcd and Rs. 2100 per capita at 40 lpcd.

Keywords

Piped water supply, rural water supply, piped network design, drinking water, domestic water, Karjat, Maharastra

Table of Contents

Content									Page Number

| Introduction |  |
| --- | --- |
| Motivation | 4 |
| 1.2 Objective and Scope | 4 |
| Norms and Investments |  |
| Norms | 5 |
| 2.2 Investments | 5 |
| Design Methodology |  |
| Components of Design | 7 |
| Assumptions | 8 |
| Design Parameters | 9 |
| 3.4 Overall Design Methodology | 10 |
| Design Details |  |
| Water Source | 17 |
| 4.2 Rising Main | 18 |
| Cost Breakdown | 19 |
| GIS Applications | 20 |
| Conclusion | 21 |
| Appendix |  |
| Village Data Summary | 22 |
| ESR Profiles for 200 LPCD Design | 24 |
| ESR Profiles for 40 LPCD Design | 152 |
| MJP Documents for Cost Estimation |  |
| ESR Construction Cost Details | 277 |
| HDPE Pipe Cost details | 282 |

- Introduction

  - Motivation

Water for domestic use is scarce in many regions across rural India, especially in the months preceding the annual monsoon rains. The Center for Technology Alternatives for Rural Areas (CTARA) at the Indian Institute of Technology Bombay (IITB) has been exploring solutions to this problem since 2005. A number of projects have been implemented in the Karjat block of Raigarh district where many of the villages north of the river Pej face severe water shortage after February.

There are two main options available for securing year-round water access for water-stressed rural communities: increasing ground water recharge and tapping into surface water. At the community level, check dams can potentially achieve both and numerous CTARA’s water related projects have centered around them. An alternative is transporting water in pipes to habitations. This project looks to assess the viability of a piped water supply system as a solution to a community’s domestic water woes.

  - Objective and Scope

Our project has two key objectives. Primarily, our aim is to assess the feasibility of a piped water distribution system for a target region spanning 120 sq. km and covering 70 villages in rural north Karjat. In addition, we aim to communicate a design methodology for a rural piped water supply system that can be applied universally. To achieve these aims have tried to design a highly optimized distribution network for north Karjat. Ours is a pre-design consisting of one primary and several secondary grids for transporting water from the water source to one point in each village in multiple stages. From estimates of the many costs of constructing and operating this network  - and the size of the population served - we can gain a sense of the techno-economic feasibility of supplying piped water to rural regions at this scale.

Ultimately, the key output of the project is not a design that can be implemented exactly as is but rather a sound pre-design from which we can confidently assess the supply system’s techno-economic feasibility. Certain salient aspects of rural water supply systems such as the distribution network within each village (tertiary grid) and potential cost-recovery plans have not been addressed in this project. Much of what follows the pre-design along the path to implementation requires a thorough study of socio-economic implications of the decisions that will need to be made. Such a study is not within the scope of this project but certainly a central theme in the projects that would follow this one.

- Norms and Investments

  - Norms

The water supplied per day per capita in piped water schemes varies across the country. The government of Mahatrashtra’s norm is 135 lpcd for urban areas and 40 lpcd for rural areas, though Mumbai receives 200 lpcd. 40 liters of water per day is just enough to cover a person’s drinking, cooking, bathing, laundry and household cleaning needs.

The current rural norm of 40 lpcd (sustenance norm) cannot provide for other uses such as home building and repairing and sustaining livelihoods. It is argued in Professor Sohoni’s lecture notes and elsewhere that there is considerable unmet demand for water in rural areas and that the rural population is willing and able to pay for additional water supply. Additional water can be used to sustain ancillary livelihoods such as livestock rearing and brick making. The additional income from these activities will enable rural consumers to pay for the water and also improve their standard of living. Thus, there is a strong argument for extending the urban norm to rural areas. In this project we have designed a pipe water distribution system for a per capita supply of both 200 lpd (livelihood norm) and 40 lpd (sustenance norm).

  - Investments

The capital cost involved in the building of a piped water distribution system include the following:

- piping

- construction of jack well and pump house

- pumping machinery

- construction of a water treatment plant

- construction of a mass balanced reservoir (MBR)

- construction of elevated storage reservoirs (ESR)

- incremental water extraction from source

The per capita investment for Mumbai’s piped water network, supplying 200 lpcd, is approximately Rs.7000. The investment for Thane (also at 200 lpcd) approaches Rs. 10,000. Maharashtra Jeevan Pradhikaran’s  Sugve and 6 Villages scheme cost approximately Rs. 2500 per capita for a supply of 40 lpcd . For our proposed supply system to be economically feasible the per capita investment would need to be well under Rs. 10,000. We must note here that there in addition to the capital investment there are the major costs of establishing the system, operation and maintenance, and of the electricity used for pumping.

- Design Methodology

  - Components of Design

The following are the major components of a rural water supply system. We have designed the primary and secondary grids such that the end point of our design are villages. A tertiary network would transport water from a single delivery point at a village to stand posts and/or individual homes. The design of the tertiary network requires consensus at the hamlet level, and includes finalizing a pay-back mechanism and metering details. In addition, the tertiary design requires cadastral data which is GIS intensive. These requirements extend beyond the scope of this project and hence we not designed tertiary networks for the system.

- Source – perennial surface water source (reservoir, river)

- Rising Main – large diameter pipeline that transports water from the source to the MBR via a water treatment plant

- Water Treatment Plant (WTP) – water treatment facility that treats raw water from the source.

- Mass Balancing Reservoir (MBR) - water tank that receives clean water coming out of the water treatment plant

- Primary Network (Gravity Main) – grid that transports water from the mass balanced reservoir to the various ESRs in the system

- Elevated Storage Reservoir (ESR) – elevated water tank that delivers water to a cluster of hamlets

- Secondary Network - grid that transports water from an ESR to one or more points (stand-posts) in the hamlets it serves

- Tertiary Network – grid that transports water from stand posts to homes in the hamlet

Layout of a typical rural piped water supply system

  - Assumptions

Three key assumptions have been made during the process of designing the network.

- Google Earth elevation data is reasonably accurate, and if there is an error it is constant across the region. Since the difference in elevation between points matters more than absolute elevation values, any constant error should not, in theory, affect the design.

- A population of 600 has been assigned to the villages whose population data we do not have. We obtained data from difference sources; our area map came from MJP, our population data from the census database. The overlap in the two sources was not perfect, we have many villages whose position we know but whose population we are not sure of. There is a good chance that the name used for a particular village differs  in the two sources. It is beyond the scope of this project, however, to research and ascertain the various identities of each village.

The number 600 was chosen at the end of an involved process of population forecasting. The 2001 census population data for each village in Karjat was projected for 2011, 2026 and 2041 using Karjat taluka’s previous years’ population data. The projected populations were rounded to the nearest hundred. We found the mode of this modified data for 2026 to be 600. We have chosen the population forecast for 2026 to calculate the water demand at each village, thus we chose to assign a 2026 population of 600 to the villages whose population we do not know.

We believe we are overestimating rather than underestimating the target area population for two reasons. If a village has a population of over 300, it is highly probably that it will be included in the census. Villages whose names are not in present the census but are marked on our map are probably small villages (population under 300) or are villages whose population has been included in a larger village. Thus, we are certain that we have overestimated the population and that given more accurate population data our network would cost less rather than more.

- The source in our design, the Pej river, has sufficient water flow at and permission has been sought to extract this water.  As we do not know the low water level  of Pej River, we have taken the depth of the jack well to be 10m. We are certain that this depth is greater than the actual required depth.

  - Design Parameters

- We have chosen one lift-up point along the Pej River which is at an elevation of 63 m. The MBR location has been chosen to be on a nearby hill at an elevation of 255 m. Water will be pumped from the life-up point to this MBR for 16 hours a day.

- From the MBR the distribution system is entirely gravity fed (no pumping required). Water will be released 24 hours a day to 19 ESRs along a primary looped MBR-ESR network.

- We have chosen to design our network such that each village receives their quota of water from an ESR within 6 hours every day: from 5-8am and 5-8pm.

- We have designed for both 40 LPCD and 200 LPCD. The cost comparisons are outlined in report.

- We have designed the primary and secondary networks such that each node served by the secondary network has a minimum pressure head of 8m. We believe this head  will be sufficient to supply water at a reasonable pressure through a tertiary network that may be built in the future.

- The pipe material we have chosen for the gravity main (primary) and distribution network (secondary) in this design is High Density Poly-Ethylene (HDPE). We chose this material because of its relatively low-cost and resistance to corrosion.

- For the rising main we have chosen ductile iron as the pipe material because it can reliably meet the main’s extreme pressure requirements.

- We have chosen a Conventional water treatment plant (WTP) as opposed to an Unconventional WTP for the network since we do not anticipate a shortage of space. Unconventional WTPs have the advantage of being more compact.

  - Overall Design Methodology

In the following section we hope to illustrate in detail our methodology of design for our piped water supply system.

- We began by using a detailed map of Karjat (obtained from Disha Kendra) to locate all villages and roads in the target region, and marked these on Google Earth.

Villages marked on Google Earth

- Next we collected and tabulated all available population data for Karjat Taluka and averaged the results of the incremental and geometric methods of population forecast to estimate the population of each village in the target area for 2026 (15 years) and 2041 (30 years).  Sample Population Forecast

- We then calculated water demand in LPS at each village for 200 LPCD and 40 LPCD given 6 hours of supply and added a 20% water loss margin.

e.g. The 2041 population of Shilar is 1126. At 200 lpcd, the demand per day in Shilar is 200 multiplied by the population, equal to 225,200lpd. This quantity is to be delivered in 6 hours supply (within 3600*6 = 21600) seconds, thus the unadjusted demand is about 10.4 LPS. We then add a 20% water loss margin to get a design demand of 12.5 LPS.

- We next decided on number of ESRs, their positions and the villages they will serve based on all of the following factors:

    - Elevation of villages - Villages with similar elevations can be served by the same ESR easily.

    - Position of villages – Piping is expensive; it is economical to place an ESR in a central location with respect to the villages it will serve.

    - Population of villages - Very large villages will perhaps need an ESR of their own, or will share an ESR with fewer than usual villages

    - Elevation of terrain - The higher the ground level elevation of the ESR, the lower the ESR height will have to be to achieve a given pressure (i.e. lower construction costs). Alternatively,  the higher the ground level elevation of the ESR, the higher the water pressure for a given ESR height be will be (i.e. lower piping costs).

    - Proximity to major road – The ESRs will be connected to the MBR along a main looped network that will consist of very large (and expensive) pipes. It is economical to minimize the length of this piping by keeping ESRs as close to the main looped network as possible. ESRs need to be position by a road also for ease of access.

    - Appearance of the land – We avoid positioning the ESR on farmland (visible on Google Earth)

Google Earth image showing proposed positions of the 19 ESRs

- Once the clusters were established we finalized the ESR-village pipe layout for each ESR-based cluster of villages as follows:

  - We drew up pipes along the roadways that connect the ESR to each village such that all marked nodes are connected to network.

  - We then assigned unique pipe and node identification numbers to each pipe and node in the system and recorded the details of village nodes (name, elevation, demand) and node-pipe connections (nodes from and to, length of the pipe)

  - We entered the above information into BRANCH 3.0, a C++ optimization programme created by the EMC and World Bank. BRANCH 3.0 calculates the lowest pipe diameters (from a user-fed list of available diameters) which will meet user-specified minimum and maximum pressure requirements.

Example of a secondary (ESR to villages) network – ESR 17

- In the next step we calculated an optimum height for the base of the water tank of the ESR. We believe this step has the potential to substantially save costs. Currently, in designs by the government the ESR height used is the minimum height at which the pressure requirement is met. However, we find that raising the height to an optimum value (which considers the drop in pipe costs due to a added pressure head) has the potential to reduce the overall cost of the project considerably.

  - We first ran BRANCH/LOOP for HGLs ranging from the minimum allowable HGL to 20 meters above the ESR ground level elevation at intervals of one meter and recorded the total pipe cost in each case. The correlation between pipe cost and ESR height (ESR Height = HGL – GL elevation of ESR) is always negative.

  - We then used an MJP document on ESR construction cost estimates to estimate the cost of constructing an ESR of a given capacity at various heights. The correlation between the cost and ESR height is positive.

  - We summed the cost of piping and ESR construction for each height increment and graphed the total cost verses ESR height. The lowest point on the graph was taken as the optimum ESR height. As you can see, an ESR height of 8m would have satisfied pressure requirements but a height of 16 can save Rs. 1.6  lakh due to the lower piping costs at this staging height.

Example of a ESR staging height optimization graph – Optimum height chosen to be 16

- We designed the MBR-ESR network, a major component of the overall design, as follows:

  - We first tested several alternative pipe layouts for connecting the MRB to each ESR and chose the layout with the lowest pipeline length and costs. This is a very time intensive and tedious process requiring the creation and running of multiple complex LOOP files.

  - We then created dummy nodes at intervals of 500-1000m and at every sharp elevation drop or rise along the finalized pipelines, and entered them into LOOP 4.0 to ensure the design incorporates dips and rises in the elevation of the terrain. This network cannot be branched due to the head loss from the dead ends being too high.

Google Earth image showing dummy nodes along primary grid

A closer look at dummy nodes (naming convention depicts distance from previous node, elevation at current node and assigned node number in that order)

- We designed the rising main as follows:

  - Different diameter inputs were selected assuming an economic velocity of 1.25 m/s.

  - Overall cost of rising main calculated for different diameters using an Excel spreadsheet provided by MJP with pre-entered formulae. The most economical diameter was selected and corresponding required pump capacity and piping were selected for the design. Rising Main Design Calculation

- Finally, we tabulated all investment costs. Used documents prepared by MJP to estimate the cost of piping, construction of ESRs, sump, and water treatment plant (WTP) and divide by total population served to obtain a value for capital cost per capita of the project.

- Design Details

  - Water Source

We considered a number of options for the water source. There are three rivers that flow in or around the target region: Ullhas, Shilar and Pej. Ullhas and Shilar are prone to drying up during the pre-monsoon months. Pej lies south of the target region and at an approximate straight-line distance of 20km to village in the target area furthest from it. It is in fact the only perennial river of the three, and our chosen water source. The water in the Pej River is supplied by a TATA power plant that lets out water in pre-determined quantities throughout the year.

Barvi Dam, built and operated by the Maharashtra Industrial Development Corporation (MIDC), seemed at one point a promising source. The enormous reservoir lies far north of the target region. We found, however, that the distance from the reservoir to the nearest point with a sufficiently high elevation was over 13km. This would require a very long rising main whose cost could substantially compromise the economic viability of the system. Furthermore, the reservoir is currently supplying water at its full capacity.

Pej River, May 1010

  - Rising Main

Two options were considered for the placement of the WTP. In the first, the WTP is placed 2.845 km from the lift-up point, and in the second the WTP is placed right next to the lift-up point. The piping cost of second option is lower by 4 crore rupees but it requires a pumping capacity that too high. Furthermore, the second option is not feasible for 40 lpcd due to high working pressure.

The following table contains the details of the rising main:

| Specification | Raw water rising main(1st stage) | Clean water rising main(2nd stage) |
| --- | --- | --- |
| Path | Lift-Up point to WTP | WTP to MBR |
| Length | 1977 m | 2845 m |
| Class of pipe | Ductile Iron | Ductile Iron |
| Diameter | 600 mm (for 200LPCD) 350 mm (for 40LPCD) | 700 mm (for 200LPCD) 350 mm (for 40LPCD) |

Google Earth image showing the relative positions of the life-up point, MBR and WTP

- Cost Breakdown

The following table contains the elements of design included in our cost estimate along with the cost breakdown.

|  |  | 200 lpcd | 40 lpcd |
| --- | --- | --- | --- |
| S.No. | Particulars | Cost(Rs.) |
| 1 | Jack Well without Over Head Pump House | 1122289 | 377287 |
| 2 | Raw Water Pumping Machinery | 1st Stage(Till 2026) | 13335000 | 2478000 |
|  |  | 2nd Stage(Till 2041) | 19488000 | 3507000 |
| 3 | Raw Water Rising Main | 34874000 | 17762000 |
| 4 | WTP | 1st Stage(Till 2026) | 24426480 | 6977800 |
|  |  | 2nd Stage(Till 2041) | 8870840 | 1973700 |
| 5 | Pure Water Pumping Machinery | 1st Stage(Till 2026) | 43512000 | 8736000 |
|  |  | 2nd Stage(Till 2041) | 55965000 | 11424000 |
| 6 | Pure Water Rising Main | 34874000 | 12343000 |
| 7 | MBR | 12446990 | 3456190 |
| 8 | Gravity Main | 137466950 | 42368560 |
| 9 | Distribution system(ESR + Pipe) | 61814926 | 21943110 |
| 10 | Excavation cost | 119569126 | 38587002 |
|  | Total | 57,21,47601 | 17,19,33649 |

The following two tables contains details on the cost per capita and the cost ratio between the 200 lpcd and 40 lpcd designs:

|  | For 200 LPCD | For 40 LPCD |
| --- | --- | --- |
| Design Population | 81,140 | 51,618 |
| Daily Demand | 19.47 MLD | 3.90 MLD |
| Net Investment | Rs. 57,21,47,601 | 17,19,33,649 |
| Cost per Person | 7051 | 2119 |
| Ratio of Design Demand | 5 | 1 |
| Ratio of Costs | 3.3 | 1 |

- GIS Application

We used Google Earth extensively at every stage of the design process. The nature of this software allowed us enormous flexibility in marking, editing, saving and sharing accumulated data, along with aiding decision making processes by providing  a visual representation of the target area.

Early in the project Google Earth was used to detect and mark villages, road networks and water sources manually. All our elevation data was obtain from Google Earth. At a later stage we used it to decide ESR locations and visually assess alternative pipe layouts. In the final stage of the design, once the pipe layout was established, we used Google Earth to ‘survey’ the terrain along our proposed pipelines. Dummy nodes were created at intervals of 500-1000m and at every major elevation rise and  dip along the pipeline. These nodes  acted as a record of elevation changes along the pipeline and were entered into LOOP 4.0 to ensure our chosen pipe diameters incorporated any head-loss due to a bumpy terrain. This latter use of GIS, we argue, holds tremendous potential to save the man-hours and high costs associated with typically pre-design land surveying.

While Google Earth has proved to be useful GIS tool for pipe network design, we believe a more optimized and streamlined design process is possible with a stronger GIS interface catered specifically towards design of piped water systems. Such an interface could include more reliable elevation data and could automate the detection of road networks, villages, uncultivated land and water sources as well as provide contour lines at small elevation intervals.

- Conclusion

Our piped water supply network design has an estimated capital cost of Rs. 2100 per capita for a demand of 40 lpcd and Rs. 7000 per capita for a demand of 200 lpcd. These numbers incorporate all major costs of building the network. Given that the per capita capital cost for Thane’s water supply scheme is Rs. 10,000 and Mumbai’s is about Rs. 7000, our findings suggest that it is indeed economically feasible to supply water in a piped network to the villages of north Karjat.

The water level at our proposed lift-up point along the Pej depends on how much the TATA Bhivpuri hydro-electric plant lets out in a given period of time. The Pej River is already being used for a piped water supply scheme, and certainly the water that flows downstream is being used by someone, in part at least. We have made the assumption in this project that there is sufficient water in the Pej river since we were not certain one way or the other (due to lack of access to data), and also because in large part our aim was to establish a universally application design methodology. Making this assumption allowed us to progress to the pre-design and fulfill part of our aim. Nevertheless, investigating the suitability of Pej river as a water source is the essential next step in CTARA’s venture to explore ways to secure water access in north Karjat.

Appendix 8.1

Village Data Summary

| S.No. | ESR # | Village | Elevation | Population |
| --- | --- | --- | --- | --- |
|  |  |  |  | 2011 | 2026 | 2041 |
| 1 | 1 | Shilar | 138 | 737 | 912 | 1126 |
| 2 |  | Unknown | 119 | 480 | 600 | 800 |
| 3 |  | Khadyrachiwadi | 133 | 480 | 600 | 800 |
| 4 |  | Kikur | 91 | 480 | 600 | 800 |
| 5 |  | Borwadi | 90 | 480 | 600 | 800 |
| 6 | 2 | Pathraj | 150 | 2058 | 2402 | 2773 |
| 7 |  | Nagyachiwadi | 158 | 480 | 600 | 800 |
| 8 | 3 | Morachiwadi | 151 | 480 | 600 | 800 |
| 9 |  | Tadwadi | 144 | 827 | 985 | 1166 |
| 10 |  | Margachiwadi | 138 | 425 | 577 | 773 |
| 11 |  | Jambhulwadi | 137 | 480 | 600 | 800 |
| 12 |  | Jalkatwadi | 150 | 480 | 600 | 800 |
| 13 |  | Dongarpada | 165 | 480 | 600 | 800 |
| 14 | 4 | Bhangarwadi | 159 | 480 | 600 | 800 |
| 15 |  | Dhabewadi | 161 | 480 | 600 | 800 |
| 16 |  | Govanwadi | 123 | 480 | 600 | 800 |
| 17 |  | Petarwadi | 136 | 480 | 600 | 800 |
| 18 |  | Ghutewadi | 121 | 480 | 600 | 800 |
| 19 | 5 | Belachiwadi | 174 | 480 | 600 | 800 |
| 20 |  | Amberpada | 166 | 480 | 600 | 800 |
| 21 |  | Katewadi | 163 | 480 | 600 | 800 |
| 22 |  | Khandas | 166 | 2637 | 2947 | 3285 |
| 23 | 6 | Mangal | 122 | 480 | 600 | 800 |
| 24 |  | Chafewadi | 129 | 1418 | 2117 | 3207 |
| 25 |  | Unknown | 113 | 480 | 600 | 800 |
| 26 |  | Jamhaiwadi | 133 | 480 | 600 | 800 |
| 27 | 7 | Nandgaon | 120 | 865 | 995 | 1137 |
| 28 |  | Daunsewadi1 | 116 | 480 | 600 | 800 |
| 29 |  | Ballvare | 117 | 1168 | 1477 | 1867 |
| 30 |  | Daunsewadi2 | 110 | 480 | 600 | 800 |
| 31 |  | Gorechiwadi | 108 | 480 | 600 | 800 |

| S.No. | ESR # | Village | Elevation | Population |
| --- | --- | --- | --- | --- |
|  |  |  |  | 2011 | 2026 | 2041 |
| 32 | 8 | Chevne | 87 | 542 | 660 | 795 |
| 33 |  | Chai | 105 | 902 | 1394 | 2173 |
| 34 |  | Kotwalwadi | 102 | 480 | 600 | 800 |
| 35 |  | Zugarachiwadi | 112 | 785 | 911 | 1047 |
| 36 | 9 | Bhopalwadi | 96 | 480 | 600 | 800 |
| 37 |  | Pendarawadi | 71 | 480 | 600 | 800 |
| 38 | 10 | Bondshet | 62 | 480 | 600 | 800 |
| 39 | 11 | Borgaon | 65 | 1095 | 1305 | 1545 |
| 40 | 12 | Aleman | 162 | 1012 | 1274 | 1587 |
| 41 |  | Telangwadi | 132 | 480 | 600 | 800 |
| 42 |  | Borichiwadi | 161 | 480 | 600 | 800 |
| 43 |  | Bhagyachiwadi | 128 | 480 | 600 | 800 |
| 44 | 13 | Murchulwadi | 153 | 480 | 600 | 800 |
| 45 |  | Bhikarwadi | 136 | 480 | 600 | 800 |
| 46 |  | Narthewadi | 119 | 480 | 600 | 800 |
| 47 | 14 | Kalamb | 50 | 4691 | 5814 | 7140 |
| 48 | 15 | Salokh | 47 | 1788 | 2165 | 2601 |
| 49 | 16 | Poshir | 45 | 2624 | 2962 | 3332 |
| 50 |  | Charnpada | 40 | 480 | 600 | 800 |
| 51 |  | Ase | 43 | 215 | 303 | 427 |
| 52 |  | Ardhe | 59 | 854 | 1062 | 1308 |
| 53 |  | Male | 53 | 1573 | 1934 | 2370 |
| 54 |  | Palanpada | 48 | 480 | 600 | 800 |
| 55 | 17 | Ware | 65 | 1755 | 2009 | 2286 |
| 56 |  | Khairpada | 54 | 480 | 600 | 800 |
| 57 |  | Mankivili | 56 | 480 | 600 | 800 |
| 58 |  | Poi | 46 | 436 | 551 | 695 |
| 59 | 18 | Chinchpada | 128 | 480 | 600 | 800 |
| 60 |  | Devpada | 87 | 480 | 600 | 800 |
| 61 |  | Giripada | 118 | 480 | 600 | 800 |
| 62 |  | Umberwadi2 | 105 | 480 | 600 | 800 |
| 63 |  | Umberwadi1 | 103 | 480 | 600 | 800 |
| 64 |  | Banjarpada | 61 | 480 | 600 | 800 |
| 65 |  | Talwade Budruk | 57 | 480 | 600 | 800 |
| 66 | 19 | Thakurwadi | 111 | 480 | 600 | 800 |
| 67 |  | Jambhulwadi | 106 | 480 | 600 | 800 |
| 68 |  | Haryachiwadi | 121 | 480 | 600 | 800 |
| 69 |  | Kurung | 96 | 650 | 765 | 899 |

Appendix - 8.2

ESR Profiles

for 200 LPCD Design

ESR 1 – Shilar

| S.No. | Village | Elevation | Population |
| --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | Shilar | 138 | 737 | 912 | 1126 |
| 2 | Unknown | 119 | 480 | 600 | 800 |
| 3 | Khadyrachiwadi | 133 | 480 | 600 | 800 |
| 4 | Kikur | 91 | 480 | 600 | 800 |
| 5 | Borwadi | 90 | 480 | 600 | 800 |
|  | Total |  | 2657 | 3312 | 4326 |

| Daily Water Demand at 200LPCD |
| --- |
| S.No. | Village | Demand(MLD) | Demand(LPS) |
|  |  | 2011 | 2041 | 2011 | 2041 |
| 1 | Shilar | 0.177 | 0.270 | 8.189 | 12.511 |
| 2 | Unknown | 0.115 | 0.192 | 5.333 | 8.889 |
| 3 | Khadyrachiwadi | 0.115 | 0.192 | 5.333 | 8.889 |
| 4 | Kikur | 0.115 | 0.192 | 5.333 | 8.889 |
| 5 | Borwadi | 0.115 | 0.192 | 5.333 | 8.889 |
|  | Total | 0.638 | 1.038 | 29.522 | 48.067 |

ESR 1 – Staging Height Optimization

| Total Daily Demand(l) | 1038240 |  |  |  |
| --- | --- | --- | --- | --- |
| ESR Capacity Required(l) | 389340 |  |  |  |
| ESR Capacity Proposed(l) | 390000 |  |  |  |
| ESR Elevation(m) | 135 |  |  |  |
| Minimum Working HGL(m) | 147 |  |  |  |
| Staging height(m) | HGL(m) | Pipe Cost | ESR Cost | Total Cost |
| 12 | 147 | 1477.73 | 1606.21 | 3083.94 |
| 13 | 148 | 1415.47 | 1638.33 | 3053.80 |
| 14 | 149 | 1380.47 | 1670.46 | 3050.93 |
| 15 | 150 | 1359.47 | 1702.58 | 3062.05 |
| 16 | 151 | 1349.16 | 1734.71 | 3083.87 |
| 17 | 152 | 1340.54 | 1782.89 | 3123.43 |
| 18 | 153 | 1333.85 | 1831.08 | 3164.93 |
| 19 | 154 | 1328.12 | 1879.27 | 3207.39 |
| 20 | 155 | 1322.39 | 1927.45 | 3249.84 |
| 21 | 156 | 1316.66 | 1991.70 | 3308.36 |
| Optimum ESR Height(m) | 14 |  |
| Tank Height(m) | 5 |  |
| Total Height of ESR(m) | 19 |  |
| ERS Cost('000 Rs.) | 1670.46 |  |
| Pipe Cost('000 Rs.) | 1380.47 |  |
| Total Cost('000 Rs.) | 3050.93 |  |
| Cost per Person(Rs.) | 705 |  |

ESR 1 – Branch Output

Echoing Input Variables

------------------------

Title of the Project                   : ESR 1

Name of the User                       :

Number of Pipes                        :  9

Number of Nodes                        :  10

Number of Commercial Diameters         :  16

Peak Design Factor                     :  1

Minimum Headloss in         m/km       :  .1

Maximum Headloss in         m/km       :  25

Minimum Residual Pressure   m          :  8

Type of Formula                        : Hazen's

Pipe Data

------------

===========================================================

Pipe  From   To     Length    Diameter  Hazen's   Status

No.  Node  Node      m         mm       Const    (E/P)

-----------------------------------------------------------

1     1     2       50.00

2     2     3      200.00

3     3     4       50.00

4     3     5     2050.00

5     2     6      340.00

6     6     7       50.00

7     6     8     1400.00

8     8     9      100.00

9     8    10      100.00

===========================================================

Node Data

-----------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

1   1.00       0.000      135.00       8.00

2   1.00       0.000      134.90       8.00

3   1.00       0.000      133.00       8.00

4   1.00     -12.511      138.00       8.00

5   1.00      -8.889      119.00       8.00

6   1.00       0.000      133.00       8.00

7   1.00      -8.889      133.00       8.00

8   1.00       0.000       85.00       8.00

Node Data  cont`d

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

9   1.00      -8.889       91.00       8.00

10   1.00      -8.889       90.00       8.00

============================================================

Reference Node Data

---------------------

===================

Node   Grade Line

No.       m

-------------------

1      149.00

===================

Commercial Diameter Data

--------------------------

====================================

Pipe Dia.   Hazen's    Unit Cost

Int. (mm)   Const    Rs /m   length

------------------------------------

63.0   140.00000       98.00

75.0   140.00000      138.00

90.0   140.00000      189.00

110.0   140.00000      270.00

125.0   140.00000      347.00

140.0   140.00000      432.00

160.0   140.00000      556.00

180.0   140.00000      695.00

200.0   140.00000      789.00

225.0   140.00000     1004.00

250.0   140.00000     1228.00

280.0   140.00000     1532.00

315.0   140.00000     1932.00

355.0   140.00000     2210.00

400.0   140.00000     3147.00

500.0   140.00000     4000.00

====================================

Branched Water Distribution Network Design Output

---------------------------------------------------

Pipe Details

--------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

1    1    2      48.067   200.0 140.00000    0.53    10.60     50.00

2    2    3      21.400   140.0 140.00000    1.35    13.35    101.16

160.0 140.00000    0.69     6.98     98.84

3    3    4      12.511   125.0 140.00000    0.43     8.60     50.00

4    3    5       8.889    90.0 140.00000    3.14    22.64    138.68

110.0 140.00000   16.29     8.52   1911.32

5    2    6      26.667   140.0 140.00000    6.83    20.09    340.00

6    6    7       8.889    90.0 140.00000    0.34    22.47     15.13

110.0 140.00000    0.30     8.60     34.87

7    6    8      17.778   125.0 140.00000   23.08    16.49   1400.00

8    8    9       8.889    90.0 140.00000    2.26    22.60    100.00

9    8   10       8.889    90.0 140.00000    2.26    22.60    100.00

============================================================================

Node Details

--------------

=============================================================================

Node    Peak Flow    Elevation    H G L    Cal Pres     Spc Pres   Meet Res

No.       (lps)        (m )        (m )      (m )         (m )    Pres. (Y)

-----------------------------------------------------------------------------

1 S       48.067     135.00     149.00      14.00         8.00

2          0.000     134.90     148.47      13.57         8.00

3          0.000     133.00     146.43      13.43         8.00

4 T      -12.511     138.00     146.00       8.00         8.00

5 T       -8.889     119.00     127.00       8.00         8.00

6          0.000     133.00     141.64       8.64         8.00

7 T       -8.889     133.00     141.00       8.00         8.00

8          0.000      85.00     118.56      33.56         8.00

9 T       -8.889      91.00     116.29      25.29         8.00

10 T       -8.889      90.00     116.29      26.29         8.00

Cost Summary

--------------

=================================================

Diameter    Length        Cost        Cum. Cost

(mm)        (m )      (1000 Rs )    (1000 Rs )

-------------------------------------------------

90.0      353.81         66.87         66.87

110.0     1946.19        525.47        592.34

125.0     1450.00        503.15       1095.49

140.0      441.16        190.58       1286.07

160.0       98.84         54.96       1341.03

200.0       50.00         39.45       1380.48

=================================================

Pipe-wise Cost Summary

------------------------

==========================================================

Pipe   Diameter      Length         Cost       Cum. Cost

No      (mm)        (m )       (1000 Rs )     (1000 Rs )

----------------------------------------------------------

1      200.0        50.00          39.45         39.45

2      140.0       101.16          43.70         83.15

160.0        98.84          54.96        138.11

3      125.0        50.00          17.35        155.46

4       90.0       138.68          26.21        181.67

110.0      1911.32         516.06        697.72

5      140.0       340.00         146.88        844.60

6       90.0        15.13           2.86        847.46

110.0        34.87           9.41        856.88

7      125.0      1400.00         485.80       1342.68

8       90.0       100.00          18.90       1361.58

9       90.0       100.00          18.90       1380.48

ESR 2 – Pathraj

| S.No. | Village | Elevation (m) |  | Population |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | Pathraj | 150 | 2058 | 2402 | 2773 |
| 2 | Nagyachiwadi | 158 | 480 | 600 | 800 |
|  | Total |  | 2538 | 3002 | 3573 |

| Daily Water Demand at 200 LPCD |
| --- |
| S.No. | Village | Demand(MLD) | Demand(LPS) |
|  |  | 2011 | 2041 | 2011 | 2041 |
| 1 | Pathraj | 0.494 | 0.666 | 22.867 | 30.811 |
| 2 | Nagyachiwadi | 0.115 | 0.192 | 5.333 | 8.889 |
|  | Total | 0.609 | 0.858 | 28.200 | 39.700 |

ESR 2 – Staging Height Optimization

| Total Demand | 857520 |  |  |  |
| --- | --- | --- | --- | --- |
| ESR capacity required | 321570 |  |  |  |
| ESR capacity proposed | 322000 |  |  |  |
| Low level Height | 172 |  |  |  |
| ESR elevation | 164 |  |  |  |
| HGL | PIPE cost | ESR cost | Total | Height (m) |
| 172 | 781.47 | 1302.545 | 2084.015 | 8 |
| 173 | 743.2 | 1330.861 | 2074.061 | 9 |
| 174 | 723.7 | 1359.178 | 2082.878 | 10 |
| 175 | 704.21 | 1387.494 | 2091.704 | 11 |
| 176 | 684.21 | 1415.81 | 2100.02 | 12 |
| 177 | 665.22 | 1444.126 | 2109.346 | 13 |
| 178 | 645.72 | 1472.442 | 2118.162 | 14 |

| ESR capacity | 322000 |
| --- | --- |
| Optimum ESR height | 9 |
| ERS cost | 1330.86 |
| Pipe cost | 743.20 |
| Total | 2074.06 |
| cost per person | 580 |

ESR 2 - BRANCH Input and Output

Echoing Input Variables

------------------------

Title of the Project                   : ESR 2

Name of the User                       :

Number of Pipes                        :  3

Number of Nodes                        :  4

Number of Commercial Diameters         :  15

Peak Design Factor                     :  1

Minimum Headloss in         m/km       :  .1

Maximum Headloss in         m/km       :  25

Minimum Residual Pressure   m          :  8

Type of Formula                        : Hazen's

Pipe Data

------------

===========================================================

Pipe  From   To     Length    Diameter  Hazen's   Status

No.  Node  Node      m         mm       Const    (E/P)

-----------------------------------------------------------

1     1     2       50.00

2     2     3      400.00

3     2     4     1400.00

===========================================================

Node Data

-----------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

1   1.00       0.000      164.00       8.00

2   1.00       0.000      163.90       8.00

3   1.00     -30.811      150.00       8.00

4   1.00      -8.889      158.00       8.00

============================================================

Reference Node Data

---------------------

===================

Node   Grade Line

No.       m

-------------------

1      173.00

Commercial Diameter Data

====================================

Pipe Dia.   Hazen's    Unit Cost

Int. (mm)   Const    Rs /m   length

------------------------------------

63.0   140.00000       98.00

75.0   140.00000      138.00

90.0   140.00000      189.00

110.0   140.00000      270.00

125.0   140.00000      347.00

140.0   140.00000      432.00

160.0   140.00000      556.00

180.0   140.00000      695.00

200.0   140.00000      789.00

225.0   140.00000     1004.00

250.0   140.00000     1228.00

280.0   140.00000     1532.00

315.0   140.00000     1932.00

355.0   140.00000     2215.00

400.0   140.00000     3147.00

====================================

Branched Water Distribution Network Design OutPut

---------------------------------------------------

Pipe Details

--------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

1    1    2      39.700   200.0 140.00000    0.37     7.40     50.00

2    2    3      30.811   160.0 140.00000    5.48    13.70    400.00

3    2    4       8.889   110.0 140.00000    0.49     8.48     57.79

125.0 140.00000    6.14     4.57   1342.21

============================================================================

Node Details

--------------

=============================================================================

Node    Peak Flow    Elevation    H G L    Cal Pres     Spc Pres   Meet Res

No.       (lps)        (m )        (m )      (m )         (m )    Pres. (Y)

-----------------------------------------------------------------------------

1 S       39.700     164.00     173.00       9.00         8.00

2          0.000     163.90     172.63       8.73         8.00

3 T      -30.811     150.00     167.15      17.15         8.00

4 T       -8.889     158.00     166.00       8.00         8.00

=============================================================================

Cost Summary

--------------

=================================================

Diameter    Length        Cost        Cum. Cost

(mm)        (m )      (1000 Rs )    (1000 Rs )

-------------------------------------------------

110.0       57.79         15.60         15.60

125.0     1342.21        465.75        481.35

160.0      400.00        222.40        703.75

200.0       50.00         39.45        743.20

=================================================

Pipe-wise Cost Summary

------------------------

==========================================================

Pipe   Diameter      Length         Cost       Cum. Cost

No      (mm)        (m )       (1000 Rs )     (1000 Rs )

----------------------------------------------------------

1      200.0        50.00          39.45         39.45

2      160.0       400.00         222.40        261.85

3      110.0        57.79          15.60        277.45

125.0      1342.21         465.75        743.20

ESR 3 – Tadwadi

| S.No. | Village | Elevation |  | Population |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | Morachiwadi | 151 | 480 | 600 | 800 |
| 2 | Tadwadi | 144 | 827 | 985 | 1166 |
| 3 | Margachiwadi | 138 | 425 | 577 | 773 |
| 4 | Jambhulwadi | 137 | 480 | 600 | 800 |
| 5 | Jalkatwadi | 150 | 480 | 600 | 800 |
| 6 | Dongarpada | 165 | 480 | 600 | 800 |
|  | Total |  | 3172 | 3962 | 5139 |

| Daily Water Demand at 200 LPCD |
| --- |
|  |  | Demand(MLD) | Demand(LPS) |
| S.No. | Village | 2011 | 2041 | 2011 | 2041 |
| 1 | Morachiwadi | 0.115 | 0.192 | 5.333 | 8.889 |
| 2 | Tadwadi | 0.198 | 0.280 | 9.189 | 12.956 |
| 3 | Margachiwadi | 0.102 | 0.186 | 4.722 | 8.589 |
| 4 | Jambhulwadi | 0.115 | 0.192 | 5.333 | 8.889 |
| 5 | Jalkatwadi | 0.115 | 0.192 | 5.333 | 8.889 |
| 6 | Dongarpada | 0.115 | 0.192 | 5.333 | 8.889 |
|  | Total | 0.761 | 1.233 | 35.244 | 57.100 |

ESR 3 – Staging Height Optimization

| Total Demand | 1233360 |  |  |  |
| --- | --- | --- | --- | --- |
| ESR capacity Required | 462510 |  |  |  |
| ESR capacity Proposed | 463000 |  |  |  |
| Low level Height | 174 |  |  |  |
| ESR elevation | 165 |  |  |  |
| HGL | PIPE cost | ESR cost | Total | Height (m) |
| 174 | 2927.5 | 1693.542 | 4621.042 | 9 |
| 175 | 2471.5 | 1729.574 | 4201.074 | 10 |
| 176 | 2214.73 | 1765.607 | 3980.337 | 11 |
| 177 | 2046.48 | 1801.64 | 3848.12 | 12 |
| 178 | 1939.68 | 1837.673 | 3777.353 | 13 |
| 179 | 1834.6 | 1873.706 | 3708.306 | 14 |
| 180 | 1751.57 | 1909.738 | 3661.308 | 15 |
| 181 | 1696.99 | 1945.771 | 3642.761 | 16 |
| ESR capacity | 463000 |  |  |  |
| Optimum ESR height | 16 |  |  |  |
| ERS cost | 1945.77 |  |  |  |
| Pipe cost | 1696.99 |  |  |  |
| Total | 3642.76 |  |  |  |
| /person | 708.846313 |  |  |  |

ESR 3 - BRANCH Input and Output

Echoing Input Variables

------------------------

Title of the Project                   : ESR 3

Name of the User                       :

Number of Pipes                        :  11

Number of Nodes                        :  12

Number of Commercial Diameters         :  15

Peak Design Factor                     :  1

Minimum Headloss in         m/km       :  .1

Maximum Headloss in         m/km       :  25

Minimum Residual Pressure   m          :  8

Type of Formula                        : Hazen's

Pipe Data

------------

===========================================================

Pipe  From   To     Length    Diameter  Hazen's   Status

No.  Node  Node      m         mm       Const    (E/P)

-----------------------------------------------------------

1     1     2      100.00

2     2     3      680.00

3     3     4       80.00

4     3     5      840.00

5     2     6      230.00

6     6     7      105.00

7     6     8      300.00

8     6     9      105.00

9     9    10      465.00

11     9    12      380.00

12    12    11     1310.00

========================================================

Node Data

-----------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

1   1.00       0.000      165.00       8.00

2   1.00       0.000      161.00       8.00

3   1.00       0.000      151.00       8.00

4   1.00      -8.889      151.00       8.00

5   1.00     -12.956      144.00       8.00

6   1.00       0.000      135.00       8.00

Node Data  cont`d

------------------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

7   1.00      -8.589      138.00       8.00

8   1.00      -8.889      137.00       8.00

9   1.00       0.000      134.00       8.00

10   1.00      -8.889      150.00       8.00

11   1.00      -8.889      165.00       8.00

12   1.00       0.000      127.00       8.00

============================================================

Reference Node Data

---------------------

===================

Node   Grade Line

No.       m

-------------------

1      181.00

===================

Commercial Diameter Data

--------------------------

====================================

Pipe Dia.   Hazen's    Unit Cost

Int. (mm)   Const    Rs /m   length

------------------------------------

63.0   140.00000       98.00

75.0   140.00000      138.00

90.0   140.00000      189.00

110.0   140.00000      270.00

125.0   140.00000      347.00

140.0   140.00000      432.00

160.0   140.00000      556.00

180.0   140.00000      695.00

200.0   140.00000      789.00

225.0   140.00000     1004.00

250.0   140.00000     1228.00

280.0   140.00000     1532.00

315.0   140.00000     1932.00

355.0   140.00000     2215.00

400.0   140.00000     3147.00

====================================

Branched Water Distribution Network Design OutPut

---------------------------------------------------

Pipe Details

--------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

1    1    2      57.101   225.0 140.00000    0.82     8.20    100.00

2    2    3      21.845   125.0 140.00000   10.28    24.13    426.01

140.0 140.00000    3.53    13.90    253.99

3    3    4       8.889    90.0 140.00000    1.81    22.63     80.00

4    3    5      12.956   110.0 140.00000   14.37    17.11    840.00

5    2    6      35.256   200.0 140.00000    1.36     5.91    230.00

6    6    7       8.589    90.0 140.00000    2.23    21.24    105.00

7    6    8       8.889    90.0 140.00000    6.79    22.63    300.00

8    6    9      17.778   160.0 140.00000    0.52     4.95    105.00

9    9   10       8.889    90.0 140.00000   10.53    22.65    465.00

11    9   12       8.889   125.0 140.00000    1.74     4.58    380.00

12   12   11       8.889   125.0 140.00000    0.27     4.66     57.99

140.0 140.00000    3.30     2.64   1252.01

============================================================================

Node Details

--------------

=============================================================================

Node    Peak Flow    Elevation    H G L    Cal Pres     Spc Pres   Meet Res

No.       (lps)        (m )        (m )      (m )         (m )    Pres. (Y)

-----------------------------------------------------------------------------

1 S       57.101     165.00     181.00      16.00         8.00

2          0.000     161.00     180.18      19.18         8.00

3          0.000     151.00     166.37      15.37         8.00

4 T       -8.889     151.00     164.56      13.56         8.00

5 T      -12.956     144.00     152.00       8.00         8.00

6          0.000     135.00     178.82      43.82         8.00

7 T       -8.589     138.00     176.59      38.59         8.00

8 T       -8.889     137.00     172.03      35.03         8.00

9          0.000     134.00     178.30      44.30         8.00

10 T       -8.889     150.00     167.77      17.77         8.00

11 T       -8.889     165.00     173.00       8.00         8.00

12          0.000     127.00     176.56      49.56         8.00

=============================================================================

Cost Summary

--------------

=================================================

Diameter    Length        Cost        Cum. Cost

(mm)        (m )      (1000 Rs )    (1000 Rs )

-------------------------------------------------

90.0      950.00        179.55        179.55

110.0      840.00        226.80        406.35

125.0      864.00        299.81        706.16

140.0     1506.00        650.59       1356.75

160.0      105.00         58.38       1415.13

200.0      230.00        181.47       1596.60

225.0      100.00        100.40       1697.00

=================================================

Pipe-wise Cost Summary

------------------------

==========================================================

Pipe   Diameter      Length         Cost       Cum. Cost

No      (mm)        (m )       (1000 Rs )     (1000 Rs )

----------------------------------------------------------

1      225.0       100.00         100.40        100.40

2      125.0       426.01         147.83        248.23

140.0       253.99         109.72        357.95

3       90.0        80.00          15.12        373.07

4      110.0       840.00         226.80        599.87

5      200.0       230.00         181.47        781.34

6       90.0       105.00          19.84        801.18

7       90.0       300.00          56.70        857.88

8      160.0       105.00          58.38        916.26

9       90.0       465.00          87.89       1004.15

11      125.0       380.00         131.86       1136.01

12      125.0        57.99          20.12       1156.13

140.0      1252.01         540.87       1697.00

ESR 4 – Bangarwadi

|  |  |  | Population |
| --- | --- | --- | --- |
| S.No. | Village | Elevation | 2011 | 2026 | 2041 |
| 1 | Bhangarwadi | 159 | 480 | 600 | 800 |
| 2 | Dhabewadi | 161 | 480 | 600 | 800 |
| 3 | Govanwadi | 123 | 480 | 600 | 800 |
| 4 | Petarwadi | 136 | 480 | 600 | 800 |
| 5 | Ghutewadi | 121 | 480 | 600 | 800 |
|  | Total |  | 2400 | 3000 | 4000 |

| Daily Water Demand at 200 LPCD |
| --- |
| S.No. | Village | Demand(MLD) | Demand(LPS) |
|  |  | 2011 | 2041 | 2011 | 2041 |
| 1 | Bhangarwadi | 0.115 | 0.192 | 5.333 | 8.889 |
| 2 | Dhabewadi | 0.115 | 0.192 | 5.333 | 8.889 |
| 3 | Govanwadi | 0.115 | 0.192 | 5.333 | 8.889 |
| 4 | Petarwadi | 0.115 | 0.192 | 5.333 | 8.889 |
| 5 | Ghutewadi | 0.115 | 0.192 | 5.333 | 8.889 |
|  | Total | 0.576 | 0.960 | 26.667 | 44.444 |

ESR 4 – Staging Height Optimization

| Total Demand | 960000 |  |  |  |
| --- | --- | --- | --- | --- |
| ESR capacity Required | 360000 |  |  |  |
| ESR capacity Proposed | 360000 |  |  |  |
| Low level Height | 184 |  |  |  |
| ESR elevation | 182 |  |  |  |
| HGL | PIPE cost | ESR cost | Total | Height |
| 184 | 1845.18 | 1095.991 | 2941.171 | 2 |
| 185 | 1827.28 | 1156.88 | 2984.16 | 3 |
| 186 | 1809.35 | 1217.768 | 3027.118 | 4 |
| 187 | 1792.83 | 1263.434 | 3056.264 | 5 |
| 188 | 1778.65 | 1309.101 | 3087.751 | 6 |
| 189 | 1767.18 | 1354.767 | 3121.947 | 7 |
| 190 | 1755.7 | 1400.433 | 3156.133 | 8 |
| 191 | 1744.24 | 1430.877 | 3175.117 | 9 |
| ESR capacity | 360000 |  |  |  |
| Optimum ESR height | 2 |  |  |  |
| ERS cost | 1095.99 |  |  |  |
| Pipe cost | 1845.18 |  |  |  |
| Total | 2941.17 |  |  |  |
| /person | 735.2928 |  |  |  |

ESR 4 - BRANCH Input and Output

Echoing Input Variables

------------------------

Title of the Project                   : ESR 4

Name of the User                       :

Number of Pipes                        :  9

Number of Nodes                        :  10

Number of Commercial Diameters         :  15

Peak Design Factor                     :  1

Minimum Headloss in         m/km       :  .1

Maximum Headloss in         m/km       :  25

Minimum Residual Pressure   m          :  8

Type of Formula                        : Hazen's

Pipe Data

------------

===========================================================

Pipe  From   To     Length    Diameter  Hazen's   Status

No.  Node  Node      m         mm       Const    (E/P)

-----------------------------------------------------------

1     1     2      200.00

2     2     3      520.00

3     3     4      150.00

4     3     5      830.00

5     2     6      500.00

6     6     7     1360.00

7     6     8     1400.00

8     8     9      500.00

9     8    10      715.00

===========================================================

Node Data

-----------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

1   1.00       0.000      182.00       8.00

2   1.00       0.000      175.00       8.00

3   1.00       0.000      157.00       8.00

4   1.00      -8.889      159.00       8.00

5   1.00      -8.889      161.00       8.00

6   1.00       0.000      160.00       8.00

7   1.00      -8.889      123.00       8.00

8   1.00       0.000      137.00       8.00

Node Data  cont`d

------------------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

9   1.00      -8.889      136.00       8.00

10   1.00      -8.889      121.00       8.00

============================================================

Reference Node Data

---------------------

===================

Node   Grade Line

No.       m

-------------------

1      184.00

===================

Commercial Diameter Data

--------------------------

====================================

Pipe Dia.   Hazen's    Unit Cost

Int. (mm)   Const    Rs /m   length

------------------------------------

63.0   140.00000       98.00

75.0   140.00000      138.00

90.0   140.00000      189.00

110.0   140.00000      270.00

125.0   140.00000      347.00

140.0   140.00000      432.00

160.0   140.00000      556.00

180.0   140.00000      695.00

200.0   140.00000      789.00

225.0   140.00000     1004.00

250.0   140.00000     1228.00

280.0   140.00000     1532.00

315.0   140.00000     1932.00

355.0   140.00000     2215.00

400.0   140.00000     3147.00

====================================

Branched Water Distribution Network Design OutPut

---------------------------------------------------

Pipe Details

--------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

1    1    2      44.445   200.0 140.00000    1.82     9.10    200.00

2    2    3      17.778   125.0 140.00000    2.76    16.51    167.13

140.0 140.00000    3.35     9.49    352.87

3    3    4       8.889    90.0 140.00000    3.40    22.67    150.00

4    3    5       8.889   110.0 140.00000    7.07     8.52    830.00

5    2    6      26.667   140.0 140.00000   10.05    20.10    500.00

6    6    7       8.889    90.0 140.00000   30.80    22.65   1360.00

7    6    8      17.778   125.0 140.00000   23.08    16.49   1400.00

8    8    9       8.889    90.0 140.00000    1.26    22.60     55.75

110.0 140.00000    3.79     8.53    444.25

9    8   10       8.889    90.0 140.00000   16.19    22.64    715.00

============================================================================

Node Details

--------------

=============================================================================

Node    Peak Flow    Elevation    H G L    Cal Pres     Spc Pres   Meet Res

No.       (lps)        (m )        (m )      (m )         (m )    Pres. (Y)

-----------------------------------------------------------------------------

1 S       44.445     182.00     184.00       2.00         8.00

2          0.000     175.00     182.18       7.18 *       8.00

3          0.000     157.00     176.07      19.07         8.00

4 T       -8.889     159.00     172.68      13.68         8.00

5 T       -8.889     161.00     169.00       8.00         8.00

6          0.000     160.00     172.13      12.13         8.00

7 T       -8.889     123.00     141.33      18.33         8.00

8          0.000     137.00     149.05      12.05         8.00

9 T       -8.889     136.00     144.00       8.00         8.00

10 T       -8.889     121.00     132.86      11.86         8.00

=============================================================================

Cost Summary

--------------

=================================================

Diameter    Length        Cost        Cum. Cost

(mm)        (m )      (1000 Rs )    (1000 Rs )

-------------------------------------------------

90.0     2280.75        431.06        431.06

110.0     1274.25        344.05        775.11

125.0     1567.13        543.79       1318.90

140.0      852.87        368.44       1687.34

200.0      200.00        157.80       1845.14

=================================================

Pipe-wise Cost Summary

------------------------

==========================================================

Pipe   Diameter      Length         Cost       Cum. Cost

No      (mm)        (m )       (1000 Rs )     (1000 Rs )

----------------------------------------------------------

1      200.0       200.00         157.80        157.80

2      125.0       167.13          57.99        215.79

140.0       352.87         152.44        368.23

3       90.0       150.00          28.35        396.58

4      110.0       830.00         224.10        620.68

5      140.0       500.00         216.00        836.68

6       90.0      1360.00         257.04       1093.72

7      125.0      1400.00         485.80       1579.52

8       90.0        55.75          10.54       1590.06

110.0       444.25         119.95       1710.01

9       90.0       715.00         135.13       1845.14

ESR 5 – Khandas

| S.No. | Village | Elevation |  | Population |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | Belachiwadi | 174 | 480 | 600 | 800 |
| 2 | Amberpada | 166 | 480 | 600 | 800 |
| 3 | Katewadi | 163 | 480 | 600 | 800 |
| 4 | Khandas | 166 | 2637 | 2947 | 3285 |
|  | Total |  | 4077 | 4747 | 5685 |

| Daily Water Demand at 200 LPCD |
| --- |
| S.No. | village | Demand(MLD) | Demand(LPS) |
|  |  | 2011 | 2041 | 2011 | 2041 |
| 1 | Belachiwadi | 0.115 | 0.192 | 5.333 | 8.889 |
| 2 | Amberpada | 0.115 | 0.192 | 5.333 | 8.889 |
| 3 | Katewadi | 0.115 | 0.192 | 5.333 | 8.889 |
| 4 | Khandas | 0.633 | 0.788 | 29.300 | 36.500 |
|  | Total | 0.978 | 1.364 | 45.300 | 63.167 |

ESR 5 – Staging Height Optimization

| Total Demand | 1364400 |  |  |  |
| --- | --- | --- | --- | --- |
| ESR capacity | 512000 |  |  |  |
| Low level Height | 183 |  |  |  |
| esr elevation | 174 |  |  |  |
| HGL | PIPE cost | ESR cost | Total | Height |
| 187 | 4571.38 | 1956.778 | 6528.158 | 13 |
| 188 | 4408.82 | 1995.146 | 6403.966 | 14 |
| 189 | 4255.29 | 2033.515 | 6288.805 | 15 |
| 190 | 4113.13 | 2071.883 | 6185.013 | 16 |
| 191 | 3984.66 | 2129.435 | 6114.095 | 17 |
| 192 | 3862.85 | 2186.987 | 6049.837 | 18 |
| 193 | 3769.34 | 2244.54 | 6013.88 | 19 |
| 194 | 3694.6 | 2302.092 | 5996.692 | 20 |
| 195 | 3637.82 | 2378.828 | 6016.648 | 21 |
| 196 | 3581.03 | 2455.565 | 6036.595 | 22 |

| ESR capacity | 512000 |
| --- | --- |
| Esr height | 20 |
| esr cost | 2455.56 |
| pipe cost | 3581.03 |
| total | 6036.59 |
| /Person cost | 1061.846 |

ESR 5 - BRANCH Input and Output

Echoing Input Variables

------------------------

Title of the Project                   : ESR 5

Name of the User                       :

Number of Pipes                        :  8

Number of Nodes                        :  9

Number of Commercial Diameters         :  16

Peak Design Factor                     :  1

Minimum Headloss in         m/km       :  .1

Maximum Headloss in         m/km       :  25

Minimum Residual Pressure   m          :  8

Type of Formula                        : Hazen's

Pipe Data

------------

===========================================================

Pipe  From   To     Length    Diameter  Hazen's   Status

No.  Node  Node      m         mm       Const    (E/P)

-----------------------------------------------------------

1     5     6      750.00

2     6     7     2080.00

3     7     8     1390.00

4     8     9      950.00

5     6     4      100.00

6     7     3      100.00

7     8     1       60.00

8     9     2      100.00

===========================================================

Node Data

-----------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

1   1.00      -8.889      174.00       8.00

2   1.00      -8.889      166.00       8.00

3   1.00      -8.889      163.00       8.00

4   1.00     -36.500      166.00       8.00

6   1.00       0.000      166.00       8.00

7   1.00       0.000      163.00       8.00

8   1.00       0.000      174.00       8.00

9   1.00       0.000      166.00       8.00

5   1.00       0.000      174.00       8.00

============================================================

Reference Node Data

---------------------

===================

Node   Grade Line

No.       m

-------------------

5      184.00

===================

Commercial Diameter Data

--------------------------

====================================

Pipe Dia.   Hazen's    Unit Cost

Int. (mm)   Const    Rs /m   length

------------------------------------

63.0   140.00000       98.00

75.0   140.00000      138.00

90.0   140.00000      189.00

110.0   140.00000      270.00

125.0   140.00000      347.00

140.0   140.00000      432.00

160.0   140.00000      556.00

180.0   140.00000      695.00

200.0   140.00000      789.00

225.0   140.00000     1004.00

250.0   140.00000     1228.00

280.0   140.00000     1532.00

315.0   140.00000     1932.00

355.0   140.00000     2210.00

400.0   140.00000     3147.00

500.0   140.00000     4000.00

====================================

Branched Water Distribution Network Design OutPut

---------------------------------------------------

Pipe Details

--------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

1    5    7      63.167   355.0 140.00000    0.80     1.07    750.00

2    7    6      36.500   200.0 140.00000    2.65     6.33    418.41

225.0 140.00000    5.92     3.56   1661.59

Pipe Details  cont`d

---------------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

3    7    8      17.778   225.0 140.00000    0.97     0.94   1027.68

250.0 140.00000    0.20     0.55    362.32

4    8    9       8.889   110.0 140.00000    6.96     8.52    816.80

125.0 140.00000    0.61     4.58    133.20

5    6    4      36.500   200.0 140.00000    0.63     6.30    100.00

6    7    3       8.889    90.0 140.00000    2.26    22.60    100.00

7    8    1       8.889   200.0 140.00000    0.03     0.50     60.00

8    9    2       8.889   125.0 140.00000    0.46     4.60    100.00

============================================================================

Node Details

--------------

=============================================================================

Node    Peak Flow    Elevation    H G L    Cal Pres     Spc Pres   Meet Res

No.       (lps)        (m )        (m )      (m )         (m )    Pres. (Y)

-----------------------------------------------------------------------------

1 T       -8.889     174.00     182.00       8.00         8.00

2 T       -8.889     166.00     174.00       8.00         8.00

3 T       -8.889     163.00     180.94      17.94         8.00

4 T      -36.500     166.00     174.00       8.00         8.00

6          0.000     166.00     174.63       8.63         8.00

7          0.000     163.00     183.20      20.20         8.00

8          0.000     174.00     182.03       8.03         8.00

9          0.000     166.00     174.46       8.46         8.00

5 S       63.167     174.00     184.00      10.00         8.00

=============================================================================

Cost Summary

--------------

=================================================

Diameter    Length        Cost        Cum. Cost

(mm)        (m )      (1000 Rs )    (1000 Rs )

-------------------------------------------------

90.0      100.00         18.90         18.90

110.0      816.80        220.54        239.44

125.0      233.20         80.92        320.36

200.0      578.41        456.36        776.72

225.0     2689.28       2700.04       3476.76

250.0      362.32        444.92       3921.68

355.0      750.00       1657.50       5579.18

=================================================

Pipe-wise Cost Summary

------------------------

==========================================================

Pipe   Diameter      Length         Cost       Cum. Cost

No      (mm)        (m )       (1000 Rs )     (1000 Rs )

----------------------------------------------------------

1      355.0       750.00        1657.50       1657.50

2      200.0       418.41         330.13       1987.63

225.0      1661.59        1668.24       3655.86

3      225.0      1027.68        1031.79       4687.65

250.0       362.32         444.93       5132.58

4      110.0       816.80         220.54       5353.12

125.0       133.20          46.22       5399.34

5      200.0       100.00          78.90       5478.24

6       90.0       100.00          18.90       5497.14

7      200.0        60.00          47.34       5544.48

8      125.0       100.00          34.70       5579.18

ESR 6 – Mangalwadi

| S.No. | Village | Elevation |  | Population |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | Mangal | 122 | 480 | 600 | 800 |
| 2 | Chafewadi | 129 | 1418 | 2117 | 3207 |
| 3 | Unknown | 113 | 480 | 600 | 800 |
| 4 | Jamhaiwadi | 133 | 480 | 600 | 800 |
|  | Total |  | 2858 | 3917 | 5607 |

| Daily Water Demand at 200 LPCD |
| --- |
| S.No. | village | Demand(MLD) | Demand(LPS) |
|  |  | 2011 | 2041 | 2011 | 2041 |
| 1 | Mangal | 0.115 | 0.192 | 5.333 | 8.889 |
| 2 | Chafewadi | 0.340 | 0.770 | 15.756 | 35.633 |
| 3 | Unknown | 0.115 | 0.192 | 5.333 | 8.889 |
| 4 | Jamhaiwadi | 0.115 | 0.192 | 5.333 | 8.889 |
|  | Total | 0.686 | 1.346 | 31.756 | 62.300 |

ESR 6 – Staging Height Optimization

| Total Demand | 1345680 |  |  |  |
| --- | --- | --- | --- | --- |
| ESR capacity Required | 504630 |  |  |  |
| ESR capacity Proposed | 505000 |  |  |  |
| Low level Height | 142 |  |  |  |
| ESR elevation | 126 |  |  |  |
| HGL | PIPE cost | ESR cost | Total | height |
| 144 | 2016.89 | 2169.352 | 4186.242 | 18 |
| 145 | 1864.48 | 2226.44 | 4090.92 | 19 |
| 146 | 1754.13 | 2283.528 | 4037.658 | 20 |
| 147 | 1656.7 | 2359.646 | 4016.346 | 21 |
| 148 | 1584.88 | 2435.763 | 4020.643 | 22 |
| 149 | 1535.57 | 2511.881 | 4047.451 | 23 |
| 150 | 1498.32 | 2587.998 | 4086.318 | 24 |
| 151 | 1463.29 | 2664.116 | 4127.406 | 25 |
| ESR capacity | 505000 |  |  |  |
| Optimum ESR height | 20 |  |  |  |
| ERS cost | 2283.53 |  |  |  |
| Pipe cost | 1754.13 |  |  |  |
| Total | 4037.66 |  |  |  |
| /person | 720.110219 |  |  |  |

ESR 6 - BRANCH Input and Output

Echoing Input Variables

------------------------

Title of the Project                   : ESR 6

Name of the User                       :

Number of Pipes                        :  8

Number of Nodes                        :  9

Number of Commercial Diameters         :  15

Peak Design Factor                     :  1

Minimum Headloss in         m/km       :  .1

Maximum Headloss in         m/km       :  25

Minimum Residual Pressure   m          :  8

Type of Formula                        : Hazen's

Pipe Data

------------

===========================================================

Pipe  From   To     Length    Diameter  Hazen's   Status

No.  Node  Node      m         mm       Const    (E/P)

-----------------------------------------------------------

1     1     2      100.00

2     2    10       60.00

3    10     3       50.00

4    10     4      850.00

5     4     5      200.00

6     4     6      470.00

7     2     7      635.00

8     7     8      800.00

===========================================================

Node Data

-----------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

1   1.00       0.000      126.00       8.00

2   1.00       0.000      125.90       8.00

3   1.00      -8.889      122.00       8.00

4   1.00       0.000      126.00       8.00

5   1.00     -35.633      129.00       8.00

6   1.00      -8.889      113.00       8.00

7   1.00       0.000       99.00       8.00

8   1.00      -8.889      133.00       8.00

10   1.00       0.000      122.00       8.00

============================================================

Reference Node Data

---------------------

===================

Node   Grade Line

No.       m

-------------------

1      146.00

===================

Commercial Diameter Data

--------------------------

====================================

Pipe Dia.   Hazen's    Unit Cost

Int. (mm)   Const    Rs /m   length

------------------------------------

63.0   140.00000       98.00

75.0   140.00000      138.00

90.0   140.00000      189.00

110.0   140.00000      270.00

125.0   140.00000      347.00

140.0   140.00000      432.00

160.0   140.00000      556.00

180.0   140.00000      695.00

200.0   140.00000      789.00

225.0   140.00000     1004.00

250.0   140.00000     1228.00

280.0   140.00000     1532.00

315.0   140.00000     1932.00

355.0   140.00000     2215.00

400.0   140.00000     3147.00

====================================

Branched Water Distribution Network Design OutPut

---------------------------------------------------

Pipe Details

--------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

1    1    2      62.300   250.0 140.00000    0.57     5.70    100.00

2    2   10      53.411   225.0 140.00000    0.43     7.17     60.00

3   10    3       8.889    90.0 140.00000    1.13    22.60     50.00

4   10    4      44.522   200.0 140.00000    5.52     9.13    604.38

Pipe Details  cont`d

---------------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

225.0 140.00000    1.26     5.13    245.62

5    4    5      35.633   200.0 140.00000    1.21     6.05    200.00

6    4    6       8.889    90.0 140.00000   10.64    22.64    470.00

7    2    7       8.889   125.0 140.00000    1.53     4.58    333.79

140.0 140.00000    0.79     2.62    301.21

8    7    8       8.889   140.0 140.00000    2.11     2.64    800.00

============================================================================

Node Details

--------------

=============================================================================

Node    Peak Flow    Elevation    H G L    Cal Pres     Spc Pres   Meet Res

No.       (lps)        (m )        (m )      (m )         (m )    Pres. (Y)

-----------------------------------------------------------------------------

1 S       62.300     126.00     146.00      20.00         8.00

2          0.000     125.90     145.43      19.53         8.00

3 T       -8.889     122.00     143.86      21.86         8.00

4          0.000     126.00     138.21      12.21         8.00

5 T      -35.633     129.00     137.00       8.00         8.00

6 T       -8.889     113.00     127.57      14.57         8.00

7          0.000      99.00     143.11      44.11         8.00

8 T       -8.889     133.00     141.00       8.00         8.00

10          0.000     122.00     144.99      22.99         8.00

=============================================================================

Cost Summary

--------------

=================================================

Diameter    Length        Cost        Cum. Cost

(mm)        (m )      (1000 Rs )    (1000 Rs )

-------------------------------------------------

90.0      520.00         98.28         98.28

125.0      333.79        115.82        214.10

140.0     1101.21        475.72        689.83

200.0      804.38        634.65       1324.48

225.0      305.62        306.85       1631.33

250.0      100.00        122.80       1754.13

=================================================

Pipe-wise Cost Summary

------------------------

==========================================================

Pipe   Diameter      Length         Cost       Cum. Cost

No      (mm)        (m )       (1000 Rs )     (1000 Rs )

----------------------------------------------------------

1      250.0       100.00         122.80        122.80

2      225.0        60.00          60.24        183.04

3       90.0        50.00           9.45        192.49

4      200.0       604.38         476.86        669.35

225.0       245.62         246.60        915.95

5      200.0       200.00         157.80       1073.75

6       90.0       470.00          88.83       1162.58

7      125.0       333.79         115.83       1278.40

140.0       301.21         130.12       1408.53

8      140.0       800.00         345.60       1754.13

ESR 7 – Nandgaon

| S.No. | village | Elevation |  | Population |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | Nandgaon | 120 | 865 | 995 | 1137 |
| 2 | Daunsewadi1 | 116 | 480 | 600 | 800 |
| 3 | Ballvare | 117 | 1168 | 1477 | 1867 |
| 4 | Daunsewadi2 | 110 | 480 | 600 | 800 |
| 5 | Gorechiwadi | 108 | 480 | 600 | 800 |
|  | Total |  | 3473 | 4272 | 5404 |

| Daily Water Demand at 200 LPCD |
| --- |
| S.No. | village | Demand(MLD) | Demand(LPS) |
|  |  | 2011 | 2041 | 2011 | 2041 |
| 1 | Nandgaon | 0.208 | 0.273 | 9.611 | 12.633 |
| 2 | Daunsewadi1 | 0.115 | 0.192 | 5.333 | 8.889 |
| 3 | Ballvare | 0.280 | 0.448 | 12.978 | 20.744 |
| 4 | Daunsewadi2 | 0.115 | 0.192 | 5.333 | 8.889 |
| 5 | Gorechiwadi | 0.115 | 0.192 | 5.333 | 8.889 |
|  | Total | 0.834 | 1.297 | 38.589 | 60.044 |

ESR 7 – Staging Height Optimization

| Total Demand | 1296960 |  |  |  |
| --- | --- | --- | --- | --- |
| ESR capacity Required | 486360 |  |  |  |
| ESR capacity Proposed | 487000 |  |  |  |
| Low level Height |  |  |  |  |
| ESR elevation | 114 |  |  |  |
| HGL | PIPE cost | ESR cost | Total | height (m) |
| 130 | 2670.51 | 2010.83 | 4681.34 | 16 |
| 131 | 2538.42 | 2066.687 | 4605.107 | 17 |
| 132 | 2424.71 | 2122.543 | 4547.253 | 18 |
| 133 | 2327 | 2178.4 | 4505.4 | 19 |
| 134 | 2241.68 | 2234.256 | 4475.936 | 20 |
| 135 | 2171.04 | 2308.731 | 4479.771 | 21 |
| 136 | 2106.24 | 2383.206 | 4489.446 | 22 |
| 137 | 2042.03 | 2457.682 | 4499.712 | 23 |
| ESR capacity | 487000 |  |  |  |
| Optimum ESR height | 20 |  |  |  |
| ERS cost | 2234.26 |  |  |  |
| Pipe cost | 2241.68 |  |  |  |
| Total | 4475.94 |  |  |  |
| /person | 828.263509 |  |  |  |

ESR 7 - BRANCH Input and Output

Echoing Input Variables

------------------------

Title of the Project                   :ESR 7

Name of the User                       :

Number of Pipes                        :  8

Number of Nodes                        :  9

Number of Commercial Diameters         :  15

Peak Design Factor                     :  1

Minimum Headloss in         m/km       :  .1

Maximum Headloss in         m/km       :  25

Minimum Residual Pressure   m          :  8

Type of Formula                        : Hazen's

Pipe Data

------------

===========================================================

Pipe  From   To     Length    Diameter  Hazen's   Status

No.  Node  Node      m         mm       Const    (E/P)

-----------------------------------------------------------

1     1     2       50.00

2     2     4      150.00

3     2     3      650.00

4     2     5      105.00

5     5     6     1950.00

6     5     7      575.00

7     7     8      210.00

8     7     9     1010.00

===========================================================

Node Data

-----------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

1   1.00       0.000      114.00       8.00

2   1.00       0.000      113.90       8.00

3   1.00     -12.633      120.00       8.00

4   1.00      -8.889      116.00       8.00

5   1.00       0.000      114.00       8.00

6   1.00     -20.744      117.00       8.00

7   1.00       0.000      106.00       8.00

8   1.00      -8.889      110.00       8.00

9   1.00      -8.889      108.00       8.00

============================================================

Reference Node Data

---------------------

===================

Node   Grade Line

No.       m

-------------------

1      134.00

===================

Commercial Diameter Data

--------------------------

====================================

Pipe Dia.   Hazen's    Unit Cost

Int. (mm)   Const    Rs /m   length

------------------------------------

63.0   140.00000       98.00

75.0   140.00000      138.00

90.0   140.00000      189.00

110.0   140.00000      270.00

125.0   140.00000      347.00

140.0   140.00000      432.00

160.0   140.00000      556.00

180.0   140.00000      695.00

200.0   140.00000      789.00

225.0   140.00000     1004.00

250.0   140.00000     1228.00

280.0   140.00000     1532.00

315.0   140.00000     1932.00

355.0   140.00000     2215.00

400.0   140.00000     3147.00

====================================

Branched Water Distribution Network Design OutPut

---------------------------------------------------

Pipe Details

--------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

1    1    2      60.044   250.0 140.00000    0.27     5.40     50.00

2    2    4       8.889    90.0 140.00000    3.40    22.67    150.00

3    2    3      12.633   110.0 140.00000    0.08    16.53      4.84

Pipe Details  cont`d

---------------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

4    2    5      38.522   200.0 140.00000    0.73     6.95    105.00

5    5    6      20.744   160.0 140.00000    1.73     6.59    262.70

180.0 140.00000    6.27     3.72   1687.30

6    5    7      17.778   125.0 140.00000    6.91    16.48    419.26

140.0 140.00000    1.48     9.50    155.74

7    7    8       8.889    90.0 140.00000    4.76    22.67    210.00

8    7    9       8.889   110.0 140.00000    8.61     8.52   1010.00

============================================================================

Node Details

--------------

=============================================================================

Node    Peak Flow    Elevation    H G L    Cal Pres     Spc Pres   Meet Res

No.       (lps)        (m )        (m )      (m )         (m )    Pres. (Y)

-----------------------------------------------------------------------------

1 S       60.044     114.00     134.00      20.00         8.00

2          0.000     113.90     133.73      19.83         8.00

3 T      -12.633     120.00     128.00       8.00         8.00

4 T       -8.889     116.00     130.34      14.34         8.00

5          0.000     114.00     133.00      19.00         8.00

6 T      -20.744     117.00     125.00       8.00         8.00

7          0.000     106.00     124.61      18.61         8.00

8 T       -8.889     110.00     119.85       9.85         8.00

9 T       -8.889     108.00     116.00       8.00         8.00

=============================================================================

Cost Summary

--------------

=================================================

Diameter    Length        Cost        Cum. Cost

(mm)        (m )      (1000 Rs )    (1000 Rs )

-------------------------------------------------

90.0      360.00         68.04         68.04

110.0     1014.84        274.01        342.05

125.0     1064.42        369.35        711.40

140.0      155.74         67.28        778.68

160.0      262.70        146.06        924.74

180.0     1687.30       1172.67       2097.42

200.0      105.00         82.85       2180.26

250.0       50.00         61.40       2241.66

=================================================

Pipe-wise Cost Summary

------------------------

==========================================================

Pipe   Diameter      Length         Cost       Cum. Cost

No      (mm)        (m )       (1000 Rs )     (1000 Rs )

----------------------------------------------------------

1      250.0        50.00          61.40         61.40

2       90.0       150.00          28.35         89.75

3      110.0         4.84           1.31         91.06

125.0       645.16         223.87        314.93

4      200.0       105.00          82.85        397.77

5      160.0       262.70         146.06        543.83

180.0      1687.30        1172.67       1716.51

6      125.0       419.26         145.48       1861.99

140.0       155.74          67.28       1929.27

7       90.0       210.00          39.69       1968.96

8      110.0      1010.00         272.70       2241.66

ESR 8 – Chai

| S.No. | village | Elevation |  | Population |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | Chevne | 87 | 542 | 660 | 795 |
| 2 | Chai | 105 | 902 | 1394 | 2173 |
| 3 | Kotwalwadi | 102 | 480 | 600 | 800 |
| 4 | Zugarachiwadi | 112 | 785 | 911 | 1047 |
|  | Total |  | 2709 | 3565 | 4815 |

| Daily Water Demand at 200 LPCD |
| --- |
| S.No. | village | Demand(MLD) | Demand(LPS) |
|  |  | 2011 | 2041 | 2011 | 2041 |
| 1 | Chevne | 0.130 | 0.191 | 6.022 | 8.833 |
| 2 | Chai | 0.216 | 0.522 | 10.022 | 24.144 |
| 3 | Kotwalwadi | 0.115 | 0.192 | 5.333 | 8.889 |
| 4 | Zugarachiwadi | 0.188 | 0.251 | 8.722 | 11.633 |
| Total |  | 0.650 | 1.156 | 30.100 | 53.500 |

ESR 8 – Staging Height Optimization

| Total Demand | 1155600 |  |  |  |
| --- | --- | --- | --- | --- |
| ESR capacity Required | 433350 |  |  |  |
| ESR capacity Proposed | 435000 |  |  |  |
| Low level Height | 121 |  |  |  |
| ESR elevation | 109 |  |  |  |
| HGL | PIPE cost | ESR cost | Total | Height of ESR |
| 131 | 3395.7 | 2216.141 | 5611.841 | 22 |
| 132 | 3284.9 | 2285.395 | 5570.295 | 23 |
| 133 | 3180.11 | 2354.65 | 5534.76 | 24 |
| 134 | 3101.15 | 2423.904 | 5525.054 | 25 |
| 135 | 3025.8 | 2493.158 | 5518.958 | 26 |
| 136 | 2964.94 | 2562.413 | 5527.353 | 27 |
| 137 | 2905.07 | 2631.667 | 5536.737 | 28 |
| 138 | 2848.98 | 2700.922 | 5549.902 | 29 |
| ESR capacity | 435000 |  |  |  |
| Optimum ESR height | 26 |  |  |  |
| ERS cost | 2493.16 |  |  |  |
| Pipe cost | 3025.80 |  |  |  |
| Total | 5518.96 |  |  |  |

ESR 8 - BRANCH Input and Output

Echoing Input Variables

------------------------

Title of the Project                   : ESR 8

Name of the User                       :

Number of Pipes                        :  8

Number of Nodes                        :  9

Number of Commercial Diameters         :  16

Peak Design Factor                     :  1

Minimum Headloss in         m/km       :  .1

Maximum Headloss in         m/km       :  25

Minimum Residual Pressure   m          :  8

Type of Formula                        : Hazen's

Pipe Data

------------

===========================================================

Pipe  From   To     Length    Diameter  Hazen's   Status

No.  Node  Node      m         mm       Const    (E/P)

-----------------------------------------------------------

1     9     5      620.00

2     5     3      180.00

3     5     6     1440.00

4     6     7      250.00

5     7     1      460.00

6     7     8      990.00

7     6     2      150.00

8     8     4       60.00

===========================================================

Node Data

-----------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

1   1.00      -8.889      102.00       8.00

2   1.00     -24.144      105.00       8.00

3   1.00      -8.833       87.00       8.00

4   1.00     -11.633      112.00       8.00

5   1.00       0.000       89.00       8.00

6   1.00       0.000       89.00       8.00

7   1.00       0.000       87.00       8.00

8   1.00       0.000      112.00       8.00

9   1.00       0.000      109.00       8.00

============================================================

Reference Node Data

---------------------

===================

Node   Grade Line

No.       m

-------------------

9      135.00

===================

Commercial Diameter Data

--------------------------

====================================

Pipe Dia.   Hazen's    Unit Cost

Int. (mm)   Const    Rs /m   length

------------------------------------

63.0   140.00000       98.00

75.0   140.00000      138.00

90.0   140.00000      189.00

110.0   140.00000      270.00

125.0   140.00000      347.00

140.0   140.00000      432.00

160.0   140.00000      556.00

180.0   140.00000      695.00

200.0   140.00000      789.00

225.0   140.00000     1004.00

250.0   140.00000     1228.00

280.0   140.00000     1532.00

315.0   140.00000     1932.00

355.0   140.00000     2210.00

400.0   140.00000     3147.00

500.0   140.00000     4000.00

====================================

Branched Water Distribution Network Design OutPut

---------------------------------------------------

Pipe Details

--------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

1    9    5      53.499   225.0 140.00000    4.48     7.23    620.00

2    5    3       8.833    90.0 140.00000    4.03    22.39    180.00

3    5    6      44.666   225.0 140.00000    7.46     5.18   1440.00

Pipe Details  cont`d

---------------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

4    6    7      20.522   180.0 140.00000    0.36     3.66     98.33

200.0 140.00000    0.33     2.18    151.67

5    7    1       8.889    90.0 140.00000   10.42    22.65    460.00

6    7    8      11.633   160.0 140.00000    2.24     2.26    990.00

7    6    2      24.144   140.0 140.00000    2.51    16.73    150.00

8    8    4      11.633   160.0 140.00000    0.14     2.33     60.00

============================================================================

Node Details

--------------

=============================================================================

Node    Peak Flow    Elevation    H G L    Cal Pres     Spc Pres   Meet Res

No.       (lps)        (m )        (m )      (m )         (m )    Pres. (Y)

-----------------------------------------------------------------------------

1 T       -8.889     102.00     111.96       9.96         8.00

2 T      -24.144     105.00     120.55      15.55         8.00

3 T       -8.833      87.00     126.49      39.49         8.00

4 T      -11.633     112.00     120.00       8.00         8.00

5          0.000      89.00     130.52      41.52         8.00

6          0.000      89.00     123.06      34.06         8.00

7          0.000      87.00     122.37      35.37         8.00

8          0.000     112.00     120.14       8.14         8.00

9 S       53.499     109.00     135.00      26.00         8.00

=============================================================================

Cost Summary

--------------

=================================================

Diameter    Length        Cost        Cum. Cost

(mm)        (m )      (1000 Rs )    (1000 Rs )

-------------------------------------------------

90.0      640.00        120.96        120.96

140.0      150.00         64.80        185.76

160.0     1050.00        583.80        769.56

180.0       98.33         68.34        837.90

200.0      151.67        119.67        957.57

225.0     2060.00       2068.24       3025.81

=================================================

Pipe-wise Cost Summary

------------------------

==========================================================

Pipe   Diameter      Length         Cost       Cum. Cost

No      (mm)        (m )       (1000 Rs )     (1000 Rs )

----------------------------------------------------------

1      225.0       620.00         622.48        622.48

2       90.0       180.00          34.02        656.50

3      225.0      1440.00        1445.76       2102.26

4      180.0        98.33          68.34       2170.60

200.0       151.67         119.67       2290.27

5       90.0       460.00          86.94       2377.21

6      160.0       990.00         550.44       2927.65

7      140.0       150.00          64.80       2992.45

8      160.0        60.00          33.36       3025.81

ESR 9 – Bhopalwadi

| S.No. | Village | Elevation |  | Population |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | Bhopalwadi | 96 | 480 | 600 | 800 |
| 2 | Pendarawadi | 71 | 480 | 600 | 800 |
|  | Total |  | 960 | 1200 | 1600 |

| Daily Water Demand at 200 LPCD |
| --- |
| S.No. | Village | Demand(MLD) | Demand(LPS) |
|  |  | 2011 | 2041 | 2011 | 2041 |
| 1 | Bhopalwadi | 0.115 | 0.192 | 5.333 | 8.889 |
| 2 | Pendarawadi | 0.115 | 0.192 | 5.333 | 8.889 |
|  | Total | 0.230 | 0.384 | 10.667 | 17.778 |

ESR 9 – Staging Height Optimization

| Total Demand | 384000 |  |  |  |
| --- | --- | --- | --- | --- |
| ESR capacity Required | 144000 |  |  |  |
| ESR capacity Proposed | 144000 |  |  |  |
| Low level Height | 105 |  |  |  |
| ESR elevation | 95 |  |  |  |
| HGL | PIPE cost | ESR cost | Total | height |
| 105 | 450.68 | 785.3424 | 1236.022 | 10 |
| 106 | 434.47 | 801.7037 | 1236.174 | 11 |
| 107 | 422.99 | 818.065 | 1241.055 | 12 |
| 108 | 416.75 | 834.4263 | 1251.176 | 13 |
| 109 | 411.01 | 850.7876 | 1261.798 | 14 |
| 110 | 405.28 | 867.1489 | 1272.429 | 15 |
| 111 | 399.55 | 883.5102 | 1283.06 | 16 |
| ESR capacity | 144000 |  |  |  |
| Optimum ESR height | 10 |  |  |  |
| ERS cost | 785.34 |  |  |  |
| Pipe cost | 450.68 |  |  |  |
| Total | 1236.02 |  |  |  |

ESR 9 - BRANCH Input and Output

Echoing Input Variables

------------------------

Title of the Project                   : ESR 9

Name of the User                       :

Number of Pipes                        :  3

Number of Nodes                        :  4

Number of Commercial Diameters         :  16

Peak Design Factor                     :  1

Minimum Headloss in         m/km       :  .1

Maximum Headloss in         m/km       :  25

Minimum Residual Pressure   m          :  8

Type of Formula                        : Hazen's

Pipe Data

------------

===========================================================

Pipe  From   To     Length    Diameter  Hazen's   Status

No.  Node  Node      m         mm       Const    (E/P)

-----------------------------------------------------------

1     1     2       50.00

2     2     3      100.00

3     2     4     1700.00

===========================================================

Node Data

-----------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

1   1.00       0.000       95.00       8.00

2   1.00       0.000       94.90       8.00

3   1.00      -8.889       96.00       8.00

4   1.00      -8.889       71.00       8.00

============================================================

Reference Node Data

---------------------

===================

Node   Grade Line

No.       m

-------------------

1      105.00

===================

Commercial Diameter Data

--------------------------

====================================

Pipe Dia.   Hazen's    Unit Cost

Int. (mm)   Const    Rs /m   length

------------------------------------

63.0   140.00000       98.00

75.0   140.00000      138.00

90.0   140.00000      189.00

110.0   140.00000      270.00

125.0   140.00000      347.00

140.0   140.00000      432.00

160.0   140.00000      556.00

180.0   140.00000      695.00

200.0   140.00000      789.00

225.0   140.00000     1004.00

250.0   140.00000     1228.00

280.0   140.00000     1532.00

315.0   140.00000     1932.00

355.0   140.00000     2210.00

400.0   140.00000     3147.00

500.0   140.00000     4000.00

====================================

Branched Water Distribution Network Design OutPut

---------------------------------------------------

Pipe Details

--------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

1    1    2      17.778   140.0 140.00000    0.47     9.40     50.00

2    2    3       8.889   110.0 140.00000    0.15     8.71     17.22

125.0 140.00000    0.38     4.59     82.78

Pipe Details  cont`d

---------------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

3    2    4       8.889    90.0 140.00000   17.70    22.65    781.42

110.0 140.00000    7.83     8.52    918.58

============================================================================

Node Details

--------------

=============================================================================

Node    Peak Flow    Elevation    H G L    Cal Pres     Spc Pres   Meet Res

No.       (lps)        (m )        (m )      (m )         (m )    Pres. (Y)

-----------------------------------------------------------------------------

1 S       17.778      95.00     105.00      10.00         8.00

2          0.000      94.90     104.53       9.63         8.00

3 T       -8.889      96.00     104.00       8.00         8.00

4 T       -8.889      71.00      79.00       8.00         8.00

=============================================================================

Cost Summary

--------------

=================================================

Diameter    Length        Cost        Cum. Cost

(mm)        (m )      (1000 Rs )    (1000 Rs )

-------------------------------------------------

90.0      781.42        147.69        147.69

110.0      935.80        252.66        400.35

125.0       82.78         28.72        429.08

140.0       50.00         21.60        450.68

=================================================

Pipe-wise Cost Summary

------------------------

==========================================================

Pipe   Diameter      Length         Cost       Cum. Cost

No      (mm)        (m )       (1000 Rs )     (1000 Rs )

----------------------------------------------------------

1      140.0        50.00          21.60         21.60

2      110.0        17.22           4.65         26.25

125.0        82.78          28.72         54.97

3       90.0       781.42         147.69        202.66

110.0       918.58         248.02        450.68

ESR 10 – Bondshet

| S.No. | village | Elevation |  | Population |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | Bondshet | 62 | 480 | 600 | 800 |
|  | Total |  | 480 | 600 | 800 |

| Daily Water Demand at 200 LPCD |
| --- |
| S.No. | village | Demand(MLD) | Demand(LPS) |
|  |  | 2011 | 2041 | 2011 | 2041 |
| 1 | Bondshet | 0.115 | 0.192 | 5.333 | 8.889 |
|  | Total | 0.115 | 0.192 | 5.333 | 8.889 |

ESR 10 Design Details

| Total Demand | 192000 |  |  |
| --- | --- | --- | --- |
| ESR capacity Required | 72000 |  |  |
| ESR capacity Proposed | 72000 |  |  |
| Low level Height | 10 |  |  |
| ESR elevation | 62 |  |  |
| HGL | ESR cost | Total | Height |
| 72 | 534.14 | 534.14 | 10 |
| ESR capacity | 72000 |  |  |
| Optimum ESR height | 10 |  |  |
| ERS cost | 534.14 |  |  |
| Total | 534.14 |  |  |
| /person | 667.675 |  |  |

ESR 11 – Borgaon

| S.No. | village | Elevation |  | Population |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | Borgaon | 65 | 1095 | 1305 | 1545 |
|  | Total |  | 1095 | 1305 | 1545 |

| Daily Water Demand at 200 LPCD |
| --- |
| S.No. | village | Demand(MLD) | Demand(LPS) |
|  |  | 2011 | 2041 | 2011 | 2041 |
| 1 | Borgaon | 0.263 | 0.371 | 12.170 | 17.163 |
|  | Total | 0.263 | 0.371 | 12.170 | 17.163 |

ESR 11 Design Details

| Total Demand | 370711 |  |  |
| --- | --- | --- | --- |
| ESR capacity Required | 139016 |  |  |
| ESR capacity Proposed | 140000 |  |  |
| Low level Height | 10 |  |  |
| ESR elevation | 65 |  |  |
| HGL | ESR cost | Total | height |
| 75 | 809.3 | 809.3 | 10 |
| ESR capacity | 140000 |  |  |
| Optimum ESR height | 10 |  |  |
| ERS cost | 809.30 |  |  |
| Total | 809.30 |  |  |
| /person | 523.945071 |  |  |

ESR 12 – Aleman

| S.No. | village | Elevation |  | Population |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | Aleman | 162 | 1012 | 1274 | 1587 |
| 2 | Telangwadi | 132 | 480 | 600 | 800 |
| 3 | Borichiwadi | 161 | 480 | 600 | 800 |
| 4 | Bhagyachiwadi | 128 | 480 | 600 | 800 |
|  | Total |  | 2452 | 3074 | 3987 |

| Daily Water Demand at 200 LPCD |
| --- |
| S.No. | village | Demand(MLD) | Demand(LPS) |
|  |  | 2011 | 2041 | 2011 | 2041 |
| 1 | Aleman | 0.243 | 0.381 | 11.248 | 17.628 |
| 2 | Telangwadi | 0.115 | 0.192 | 5.333 | 8.889 |
| 3 | Borichiwadi | 0.115 | 0.192 | 5.333 | 8.889 |
| 4 | Bhagyachiwadi | 0.115 | 0.192 | 5.333 | 8.889 |
|  | Total | 0.589 | 0.957 | 27.248 | 44.295 |

ESR 12 – Staging Height Optimization

| Total Demand | 956773 |  |  |  |
| --- | --- | --- | --- | --- |
| ESR capacity Required | 358790 |  |  |  |
| ESR capacity Proposed | 360000 |  |  |  |
| Low level Height | 173 |  |  |  |
| ESR elevation | 165 |  |  |  |
| HGL | PIPE cost | ESR cost | Total | height |
| 176 | 1977.89 | 1491.766 | 3469.656 | 11 |
| 177 | 1925.28 | 1522.21 | 3447.49 | 12 |
| 178 | 1892.23 | 1552.654 | 3444.884 | 13 |
| 179 | 1859.18 | 1583.098 | 3442.278 | 14 |
| 180 | 1826.13 | 1613.543 | 3439.673 | 15 |
| 181 | 1793.07 | 1643.987 | 3437.057 | 16 |
| 182 | 1760.03 | 1689.653 | 3449.683 | 17 |
| 183 | 1727.46 | 1735.319 | 3462.779 | 18 |
| 184 | 1704.89 | 1780.986 | 3485.876 | 19 |
| 185 | 1687.01 | 1826.652 | 3513.662 | 20 |
| Optimum ESR height | 16 |  |  |  |
| ERS cost | 1643.99 |  |  |  |
| Pipe cost | 1793.07 |  |  |  |
| Total | 3437.06 |  |  |  |
| /person | 862 |  |  |  |

ESR 12 - BRANCH Input and Output

Echoing Input Variables

------------------------

Title of the Project                   :ESR 12

Name of the User                       :

Number of Pipes                        :  7

Number of Nodes                        :  8

Number of Commercial Diameters         :  16

Peak Design Factor                     :  1

Minimum Headloss in         m/km       :  .1

Maximum Headloss in         m/km       :  25

Minimum Residual Pressure   m          :  8

Type of Formula                        : Hazen's

Pipe Data

------------

===========================================================

Pipe  From   To     Length    Diameter  Hazen's   Status

No.  Node  Node      m         mm       Const    (E/P)

-----------------------------------------------------------

1     1     2       50.00

2     2     3      150.00

3     2     4     2000.00

4     2     5      765.00

5     5     6      565.00

6     6     7      150.00

7     6     8     2555.00

===========================================================

Node Data

-----------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

1   1.00       0.000      165.00       8.00

2   1.00       0.000      164.90       8.00

3   1.00     -17.628      162.00       8.00

4   1.00      -8.889      132.00       8.00

5   1.00       0.000      160.00       8.00

6   1.00       0.000      161.00       8.00

7   1.00      -8.889      161.00       8.00

8   1.00      -8.889      128.00       8.00

============================================================

Reference Node Data

---------------------

===================

Node   Grade Line

No.       m

-------------------

1      181.00

===================

Commercial Diameter Data

--------------------------

====================================

Pipe Dia.   Hazen's    Unit Cost

Int. (mm)   Const    Rs /m   length

------------------------------------

63.0   140.00000       98.00

75.0   140.00000      138.00

90.0   140.00000      189.00

110.0   140.00000      270.00

125.0   140.00000      347.00

140.0   140.00000      432.00

160.0   140.00000      556.00

180.0   140.00000      695.00

200.0   140.00000      789.00

225.0   140.00000     1004.00

250.0   140.00000     1228.00

280.0   140.00000     1532.00

315.0   140.00000     1932.00

355.0   140.00000     2210.00

400.0   140.00000     3147.00

500.0   140.00000     4000.00

====================================

Branched Water Distribution Network Design OutPut

---------------------------------------------------

Pipe Details

--------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

1    1    2      44.295   200.0 140.00000    0.45     9.00     50.00

2    2    3      17.628   125.0 140.00000    2.43    16.20    150.00

3    2    4       8.889    90.0 140.00000   37.68    22.64   1664.01

Pipe Details  cont`d

---------------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

110.0 140.00000    2.86     8.51    335.99

4    2    5      17.778   140.0 140.00000    7.26     9.49    765.00

5    5    6      17.778   140.0 140.00000    1.67     9.48    176.22

160.0 140.00000    1.93     4.96    388.78

6    6    7       8.889   125.0 140.00000    0.69     4.60    150.00

7    6    8       8.889    90.0 140.00000   19.10    22.65    843.28

110.0 140.00000   14.59     8.52   1711.72

============================================================================

Node Details

--------------

=============================================================================

Node    Peak Flow    Elevation    H G L    Cal Pres     Spc Pres   Meet Res

No.       (lps)        (m )        (m )      (m )         (m )    Pres. (Y)

-----------------------------------------------------------------------------

1 S       44.295     165.00     181.00      16.00         8.00

2          0.000     164.90     180.55      15.65         8.00

3 T      -17.628     162.00     178.11      16.11         8.00

4 T       -8.889     132.00     140.00       8.00         8.00

5          0.000     160.00     173.29      13.29         8.00

6          0.000     161.00     169.69       8.69         8.00

7 T       -8.889     161.00     169.00       8.00         8.00

8 T       -8.889     128.00     136.00       8.00         8.00

=============================================================================

Cost Summary

--------------

=================================================

Diameter    Length        Cost        Cum. Cost

(mm)        (m )      (1000 Rs )    (1000 Rs )

-------------------------------------------------

90.0     2507.30        473.88        473.88

110.0     2047.70        552.88       1026.76

125.0      300.00        104.10       1130.86

140.0      941.22        406.61       1537.47

160.0      388.78        216.16       1753.63

200.0       50.00         39.45       1793.08

=================================================

Pipe-wise Cost Summary

------------------------

==========================================================

Pipe   Diameter      Length         Cost       Cum. Cost

No      (mm)        (m )       (1000 Rs )     (1000 Rs )

----------------------------------------------------------

1      200.0        50.00          39.45         39.45

2      125.0       150.00          52.05         91.50

3       90.0      1664.01         314.50        406.00

110.0       335.99          90.72        496.72

4      140.0       765.00         330.48        827.20

5      140.0       176.22          76.13        903.32

160.0       388.78         216.16       1119.48

6      125.0       150.00          52.05       1171.53

7       90.0       843.28         159.38       1330.91

110.0      1711.72         462.16       1793.08

ESR 13 – Murchulwadi

| S.No. | village | Elevation |  | Population |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | Murchulwadi | 153 | 480 | 600 | 800 |
| 2 | Bhikarwadi | 136 | 480 | 600 | 800 |
| 3 | Narthewadi | 119 | 480 | 600 | 800 |
|  | Total |  | 1440 | 1800 | 2400 |

| Daily Water Demand at 200 LPCD |
| --- |
| S.No. |  | Demand(MLD) |  | Demand(LPS) |  |
|  | village | 2011 | 2041 | 2011 | 2041 |
| 1 | Murchulwadi | 0.115 | 0.192 | 5.333 | 8.889 |
| 2 | Bhikarwadi | 0.115 | 0.192 | 5.333 | 8.889 |
| 3 | Narthewadi | 0.115 | 0.192 | 5.333 | 8.889 |
|  | Total | 0.346 | 0.576 | 16.000 | 26.667 |

ESR 13 – Staging Height Optimization

| Total Demand | 576000 |  |  |  |
| --- | --- | --- | --- | --- |
| ESR capacity Required | 216000 |  |  |  |
| ESR capacity Proposed | 216000 |  |  |  |
| Low level Height | 162 |  |  |  |
| ESR elevation | 153 |  |  |  |
| HGL | PIPE cost | ESR cost | Total | Height (m) |
| 162 | 927.59 | 1016.262 | 1943.852 | 9 |
| 163 | 895.63 | 1037.885 | 1933.515 | 10 |
| 164 | 878.69 | 1059.507 | 1938.197 | 11 |
| 165 | 866.81 | 1081.13 | 1947.94 | 12 |
| 166 | 855.34 | 1102.753 | 1958.093 | 13 |
| 167 | 847.27 | 1124.375 | 1971.645 | 14 |
| 168 | 841.53 | 1145.998 | 1987.528 | 15 |
| Optimum ESR height | 10 |  |  |  |
| ERS cost | 1037.88 |  |  |  |
| Pipe cost | 895.63 |  |  |  |
| Total | 1933.51 |  |  |  |
| /person | 806 |  |  |  |

ESR 13 - BRANCH Input and Output

Echoing Input Variables

------------------------

Title of the Project                   : ESR 13

Name of the User                       :

Number of Pipes                        :  6

Number of Nodes                        :  7

Number of Commercial Diameters         :  16

Peak Design Factor                     :  1

Minimum Headloss in         m/km       :  .1

Maximum Headloss in         m/km       :  25

Minimum Residual Pressure   m          :  8

Type of Formula                        : Hazen's

Pipe Data

------------

===========================================================

Pipe  From   To     Length    Diameter  Hazen's   Status

No.  Node  Node      m         mm       Const    (E/P)

-----------------------------------------------------------

1     1     2      100.00

2     2     3      150.00

3     2     4      850.00

4     4     5      150.00

5     4     6     1700.00

6     6     7      150.00

===========================================================

Node Data

-----------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

1   1.00       0.000      153.00       8.00

2   1.00       0.000      152.90       8.00

3   1.00      -8.889      153.00       8.00

4   1.00       0.000      134.00       8.00

5   1.00      -8.889      136.00       8.00

6   1.00       0.000      119.00       8.00

7   1.00      -8.889      119.00       8.00

============================================================

Reference Node Data

---------------------

===================

Node   Grade Line

No.       m

-------------------

1      163.00

===================

Commercial Diameter Data

--------------------------

====================================

Pipe Dia.   Hazen's    Unit Cost

Int. (mm)   Const    Rs /m   length

------------------------------------

63.0   140.00000       98.00

75.0   140.00000      138.00

90.0   140.00000      189.00

110.0   140.00000      270.00

125.0   140.00000      347.00

140.0   140.00000      432.00

160.0   140.00000      556.00

180.0   140.00000      695.00

200.0   140.00000      789.00

225.0   140.00000     1004.00

250.0   140.00000     1228.00

280.0   140.00000     1532.00

315.0   140.00000     1932.00

355.0   140.00000     2210.00

400.0   140.00000     3147.00

500.0   140.00000     4000.00

====================================

Branched Water Distribution Network Design OutPut

---------------------------------------------------

Pipe Details

--------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

1    1    2      26.667   160.0 140.00000    1.05    10.50    100.00

2    2    3       8.889   110.0 140.00000    0.57     8.49     67.11

125.0 140.00000    0.38     4.58     82.89

Pipe Details  cont`d

---------------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

3    2    4      17.778   125.0 140.00000   14.01    16.48    850.00

4    4    5       8.889    90.0 140.00000    3.40    22.67    150.00

5    4    6       8.889    90.0 140.00000    4.89    22.63    216.11

110.0 140.00000   12.65     8.52   1483.89

6    6    7       8.889    90.0 140.00000    3.40    22.67    150.00

============================================================================

Node Details

--------------

=============================================================================

Node    Peak Flow    Elevation    H G L    Cal Pres     Spc Pres   Meet Res

No.       (lps)        (m )        (m )      (m )         (m )    Pres. (Y)

-----------------------------------------------------------------------------

1 S       26.667     153.00     163.00      10.00         8.00

2          0.000     152.90     161.95       9.05         8.00

3 T       -8.889     153.00     161.00       8.00         8.00

4          0.000     134.00     147.94      13.94         8.00

5 T       -8.889     136.00     144.54       8.54         8.00

6          0.000     119.00     130.40      11.40         8.00

7 T       -8.889     119.00     127.00       8.00         8.00

=============================================================================

Cost Summary

--------------

=================================================

Diameter    Length        Cost        Cum. Cost

(mm)        (m )      (1000 Rs )    (1000 Rs )

-------------------------------------------------

90.0      516.11         97.54         97.54

110.0     1551.00        418.77        516.31

125.0      932.89        323.71        840.03

160.0      100.00         55.60        895.63

=================================================

Pipe-wise Cost Summary

------------------------

==========================================================

Pipe   Diameter      Length         Cost       Cum. Cost

No      (mm)        (m )       (1000 Rs )     (1000 Rs )

----------------------------------------------------------

1      160.0       100.00          55.60         55.60

2      110.0        67.11          18.12         73.72

125.0        82.89          28.76        102.48

3      125.0       850.00         294.95        397.43

4       90.0       150.00          28.35        425.78

5       90.0       216.11          40.84        466.63

110.0      1483.89         400.65        867.28

6       90.0       150.00          28.35        895.63

ESR 14 – Kalamb

| S.No. | village | Elevation |  | Population |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | Kalamb | 50 | 4691 | 5814 | 7140 |
|  | Total |  | 4691 | 5814 | 7140 |

| Daily Water Demand at 200 LPCD |
| --- |
| S.No. | village | Demand(MLD) | Demand(LPS) |
|  |  | 2011 | 2041 | 2011 | 2041 |
| 1 | Kalamb | 1.126 | 1.714 | 52.125 | 79.334 |
|  | Total | 1.126 | 1.714 | 52.125 | 79.334 |

ESR 14 Design Details

| Total Demand | 1713605 |  |  |
| --- | --- | --- | --- |
| ESR capacity Required | 642602 |  |  |
| ESR capacity Proposed | 645000 |  |  |
| Low level height | 14 |  |  |
| ESR elevation | 43 |  |  |
| HGL | ESR cost | Total | height |
| 57 | 2300.84 | 2300.84 | 14 |
| ESR capacity | 645000 |  |  |
| Optimum ESR height | 14 |  |  |
| ERS cost | 2300.84 |  |  |
| Total | 2300.84 |  |  |
| /person | 322.25 |  |  |

ESR 15 – Salokh

| S.No. | Village | Elevation |  | Population |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | Salokh | 47 | 1788 | 2165 | 2601 |
|  | Total |  | 1788 | 2165 | 2601 |

| Daily Water Demand at 200 LPCD |
| --- |
| S.No. | village | Demand(MLD) | Demand(LPS) |
|  |  | 2011 | 2041 | 2011 | 2041 |
| 1 | Salokh | 0.429 | 0.624 | 19.867 | 28.900 |
|  | Total | 0.429 | 0.624 | 19.867 | 28.900 |

ESR 15 Design Details

| Total Demand | 624240 |  |  |
| --- | --- | --- | --- |
| ESR capacity Required | 234090 |  |  |
| ESR capacity Proposed | 235000 |  |  |
| Low level height | 10 |  |  |
| ESR elevation | 47 |  |  |
| HGL | ESR cost | Total | height |
| 57 | 1098.26 | 1098.26 | 10 |
| ESR capacity | 72000 |  |  |
| Optimum ESR height | 12 |  |  |
| ERS cost | 1098.26 |  |  |
| Total | 1098.26 |  |  |
| /person | 422.25 |  |  |

ESR 16 – Male

| S.No. | Village | Elevation |  | Population |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | Poshir | 45 | 2624 | 2962 | 3332 |
| 2 | Charnpada | 40 | 480 | 600 | 800 |
| 3 | Ase | 43 | 215 | 303 | 427 |
| 4 | Ardhe | 59 | 854 | 1062 | 1308 |
| 5 | Male | 53 | 1573 | 1934 | 2370 |
| 6 | Palanpada | 48 | 480 | 600 | 800 |
|  | Total |  | 6226 | 7461 | 9038 |

| Daily Water Demand at 200 LPCD |
| --- |
| S.No. | Village | Demand(MLD) | Demand(LPS) |
|  |  | 2011 | 2041 | 2011 | 2041 |
| 1 | Poshir | 0.630 | 0.800 | 29.151 | 37.026 |
| 2 | Charnpada | 0.115 | 0.192 | 5.333 | 8.889 |
| 3 | Ase | 0.052 | 0.103 | 2.389 | 4.749 |
| 4 | Ardhe | 0.205 | 0.314 | 9.491 | 14.532 |
| 5 | Male | 0.378 | 0.569 | 17.483 | 26.335 |
| 6 | Palanpada | 0.115 | 0.192 | 5.333 | 8.889 |
|  | Total | 1.494 | 2.169 | 69.180 | 100.420 |

ESR 16 – Staging Height Optimization

| Total Demand | 2169080 |  |  |  |
| --- | --- | --- | --- | --- |
| ESR capacity Required | 813405 |  |  |  |
| ESR capacity Proposed | 816000 |  |  |  |
| Low level Height | 68 |  |  |  |
| ESR elevation | 56 |  |  |  |
| HGL | PIPE cost | ESR cost | Total | height |
| 70 | 3707.03 | 2765.438 | 6472.468 | 14 |
| 71 | 3554.84 | 2818.62 | 6373.46 | 15 |
| 72 | 3410.71 | 2871.801 | 6282.511 | 16 |
| 73 | 3292.06 | 2951.573 | 6243.633 | 17 |
| 74 | 3184.76 | 3031.346 | 6216.106 | 18 |
| 75 | 3096.82 | 3111.118 | 6207.938 | 19 |
| 76 | 3021.43 | 3190.89 | 6212.32 | 20 |
| 77 | 2953.56 | 3297.253 | 6250.813 | 21 |
| 78 | 2903.74 | 3403.616 | 6307.356 | 22 |
| ESR capacity | 816000 |  |  |  |
| Optimum ESR height | 19 |  |  |  |
| ERS cost | 3111.12 |  |  |  |
| Pipe cost | 3096.82 |  |  |  |
| Total | 6207.94 |  |  |  |
| /person | 686.88 |  |  |  |

ESR 16 - BRANCH Input and Output

Echoing Input Variables

------------------------

Title of the Project                   :ESR 16

Name of the User                       :

Number of Pipes                        :  12

Number of Nodes                        :  13

Number of Commercial Diameters         :  16

Peak Design Factor                     :  1

Minimum Headloss in         m/km       :  .1

Maximum Headloss in         m/km       :  25

Minimum Residual Pressure   m          :  8

Type of Formula                        : Hazen's

Pipe Data

------------

===========================================================

Pipe  From   To     Length    Diameter  Hazen's   Status

No.  Node  Node      m         mm       Const    (E/P)

-----------------------------------------------------------

1    11    12       50.00

2    12     7      460.00

3    12     6      240.00

4     7     8      940.00

5     6     9     1450.00

6     9    10      400.00

7    10     1      360.00

8     9     2       70.00

9     6     5       70.00

10     8     4      130.00

11     7     3       20.00

12     6    13      760.00

===========================================================

Node Data

-----------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

1   1.00     -37.026       45.00       8.00

2   1.00      -8.889       40.00       8.00

3   1.00      -4.749       43.00       8.00

4   1.00     -14.532       59.00       8.00

5   1.00     -26.335       53.00       8.00

Node Data  cont`d

------------------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

6   1.00       0.000       45.00       8.00

7   1.00       0.000       41.00       8.00

8   1.00       0.000       43.00       8.00

9   1.00       0.000       27.00       8.00

10   1.00       0.000       35.00       8.00

11   1.00       0.000       56.00       8.00

12   1.00       0.000       55.90       8.00

13   1.00      -8.889       48.00       8.00

============================================================

Reference Node Data

---------------------

===================

Node   Grade Line

No.       m

-------------------

11       75.00

===================

Commercial Diameter Data

--------------------------

====================================

Pipe Dia.   Hazen's    Unit Cost

Int. (mm)   Const    Rs /m   length

------------------------------------

63.0   140.00000       98.00

75.0   140.00000      138.00

90.0   140.00000      189.00

110.0   140.00000      270.00

125.0   140.00000      347.00

140.0   140.00000      432.00

160.0   140.00000      556.00

180.0   140.00000      695.00

200.0   140.00000      789.00

225.0   140.00000     1004.00

250.0   140.00000     1228.00

280.0   140.00000     1532.00

315.0   140.00000     1932.00

355.0   140.00000     2210.00

400.0   140.00000     3147.00

500.0   140.00000     4000.00

====================================

Pipe Details

--------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

1   11   12     100.420   280.0 140.00000    0.40     8.00     50.00

2   12    7      19.281   160.0 140.00000    2.65     5.76    460.00

3   12    6      81.139   225.0 140.00000    1.00    15.65     63.90

250.0 140.00000    1.65     9.37    176.10

4    7    8      14.532   140.0 140.00000    1.87     6.53    286.30

160.0 140.00000    2.23     3.41    653.70

5    6    9      45.915   200.0 140.00000   14.02     9.67   1450.00

6    9   10      37.026   200.0 140.00000    2.60     6.50    400.00

7   10    1      37.026   200.0 140.00000    2.34     6.50    360.00

8    9    2       8.889    90.0 140.00000    1.59    22.71     70.00

9    6    5      26.335   140.0 140.00000    1.37    19.57     70.00

10    8    4      14.532   140.0 140.00000    0.85     6.54    130.00

11    7    3       4.749    75.0 140.00000    0.35    17.50     20.00

12    6   13       8.889    90.0 140.00000   15.20    22.65    671.08

110.0 140.00000    0.76     8.55     88.92

============================================================================

Node Details

--------------

=============================================================================

Node    Peak Flow    Elevation    H G L    Cal Pres     Spc Pres   Meet Res

No.       (lps)        (m )        (m )      (m )         (m )    Pres. (Y)

-----------------------------------------------------------------------------

1 T      -37.026      45.00      53.00       8.00         8.00

2 T       -8.889      40.00      56.35      16.35         8.00

3 T       -4.749      43.00      71.61      28.61         8.00

4 T      -14.532      59.00      67.00       8.00         8.00

5 T      -26.335      53.00      70.58      17.58         8.00

6          0.000      45.00      71.96      26.96         8.00

7          0.000      41.00      71.95      30.95         8.00

8          0.000      43.00      67.85      24.85         8.00

9          0.000      27.00      57.94      30.94         8.00

10          0.000      35.00      55.34      20.34         8.00

11 S      100.420      56.00      75.00      19.00         8.00

12          0.000      55.90      74.60      18.70         8.00

13 T       -8.889      48.00      56.00       8.00         8.00

=============================================================================

Cost Summary

--------------

=================================================

Diameter    Length        Cost        Cum. Cost

(mm)        (m )      (1000 Rs )    (1000 Rs )

-------------------------------------------------

75.0       20.00          2.76          2.76

90.0      741.08        140.06        142.82

110.0       88.92         24.01        166.83

140.0      486.30        210.08        376.91

160.0     1113.70        619.22        996.13

200.0     2210.00       1743.69       2739.82

225.0       63.90         64.15       2803.97

250.0      176.10        216.25       3020.23

280.0       50.00         76.60       3096.83

=================================================

Pipe-wise Cost Summary

------------------------

==========================================================

Pipe   Diameter      Length         Cost       Cum. Cost

No      (mm)        (m )       (1000 Rs )     (1000 Rs )

----------------------------------------------------------

1      280.0        50.00          76.60         76.60

2      160.0       460.00         255.76        332.36

3      225.0        63.90          64.16        396.52

250.0       176.10         216.25        612.77

4      140.0       286.30         123.68        736.45

160.0       653.70         363.46       1099.91

5      200.0      1450.00        1144.05       2243.96

6      200.0       400.00         315.60       2559.56

7      200.0       360.00         284.04       2843.60

8       90.0        70.00          13.23       2856.83

9      140.0        70.00          30.24       2887.07

10      140.0       130.00          56.16       2943.23

11       75.0        20.00           2.76       2945.99

12       90.0       671.08         126.83       3072.82

110.0        88.92          24.01       3096.83

ESR 17 – Vara

| S.No. | village | Elevation |  | Population |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | ware | 65 | 1755 | 2009 | 2286 |
| 2 | khairpada | 54 | 480 | 600 | 800 |
| 3 | mankivili | 56 | 480 | 600 | 800 |
| 4 | poi | 46 | 436 | 551 | 695 |
|  | Total |  | 3151 | 3760 | 4581 |

| Daily Water Demand at 200 LPCD |
| --- |
| S.No. | village | Demand(MLD) | Demand(LPS) |
|  |  | 2011 | 2041 | 2011 | 2041 |
| 1 | ware | 0.421 | 0.549 | 19.495 | 25.405 |
| 2 | khairpada | 0.115 | 0.192 | 5.333 | 8.889 |
| 3 | mankivili | 0.115 | 0.192 | 5.333 | 8.889 |
| 4 | poi | 0.105 | 0.167 | 4.848 | 7.719 |
| Total |  | 0.756 | 1.099 | 35.010 | 50.902 |

ESR 17 – Staging Height Optimization

| Total Demand | 1099476 |  |  |  |
| --- | --- | --- | --- | --- |
| ESR capacity Required | 412303 |  |  |  |
| ESR capacity Proposed | 413000 |  |  |  |
| Low level Height | 74 |  |  |  |
| ESR elevation | 58 |  |  |  |
| HGL | PIPE cost | ESR cost | Total | height |
| 74 | 1710.68 | 1810.231 | 3520.911 | 16 |
| 75 | 1638.9 | 1860.515 | 3499.415 | 17 |
| 76 | 1583.51 | 1910.8 | 3494.31 | 18 |
| 77 | 1536.72 | 1961.084 | 3497.804 | 19 |
| 78 | 1496.39 | 2011.368 | 3507.758 | 20 |
| 79 | 1468.02 | 2078.414 | 3546.434 | 21 |
| 80 | 1449.03 | 2145.459 | 3594.489 | 22 |
| 81 | 1430.11 | 2212.505 | 3642.615 | 23 |
| 82 | 1411.19 | 2279.55 | 3690.74 | 24 |
| ESR capacity | 413000 |  |  |  |
| Optimum ESR height | 18 |  |  |  |
| ERS cost | 1910.80 |  |  |  |
| Pipe cost | 1583.51 |  |  |  |
| Total | 3494.31 |  |  |  |
| /person | 762.76 |  |  |  |

ESR 17 - BRANCH Input and Output

Echoing Input Variables

------------------------

Title of the Project                   :ESR 17

Name of the User                       :

Number of Pipes                        :  7

Number of Nodes                        :  8

Number of Commercial Diameters         :  16

Peak Design Factor                     :  1

Minimum Headloss in         m/km       :  .1

Maximum Headloss in         m/km       :  25

Minimum Residual Pressure   m          :  8

Type of Formula                        : Hazen's

Pipe Data

------------

===========================================================

Pipe  From   To     Length    Diameter  Hazen's   Status

No.  Node  Node      m         mm       Const    (E/P)

-----------------------------------------------------------

1     1     2       50.00

2     2     3      220.00

3     2     4      710.00

4     4     5      760.00

5     4     6       75.00

6     6     7      775.00

7     6     8     2000.00

===========================================================

Node Data

-----------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

1   1.00       0.000       58.00       8.00

2   1.00       0.000       57.90       8.00

3   1.00     -25.405       65.00       8.00

4   1.00       0.000       50.00       8.00

5   1.00      -8.889       54.00       8.00

6   1.00       0.000       51.00       8.00

7   1.00      -8.889       56.00       8.00

8   1.00      -7.719       46.00       8.00

============================================================

Reference Node Data

---------------------

===================

Node   Grade Line

No.       m

-------------------

1       76.00

===================

Commercial Diameter Data

--------------------------

====================================

Pipe Dia.   Hazen's    Unit Cost

Int. (mm)   Const    Rs /m   length

------------------------------------

63.0   140.00000       98.00

75.0   140.00000      138.00

90.0   140.00000      189.00

110.0   140.00000      270.00

125.0   140.00000      347.00

140.0   140.00000      432.00

160.0   140.00000      556.00

180.0   140.00000      695.00

200.0   140.00000      789.00

225.0   140.00000     1004.00

250.0   140.00000     1228.00

280.0   140.00000     1532.00

315.0   140.00000     1932.00

355.0   140.00000     2210.00

400.0   140.00000     3147.00

500.0   140.00000     4000.00

====================================

Branched Water Distribution Network Design OutPut

---------------------------------------------------

Pipe Details

--------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

1    1    2      50.902   225.0 140.00000    0.33     6.60     50.00

2    2    3      25.405   140.0 140.00000    1.17    18.34     63.80

160.0 140.00000    1.50     9.60    156.20

Pipe Details  cont`d

---------------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

3    2    4      25.497   160.0 140.00000    6.85     9.65    710.00

4    4    5       8.889    90.0 140.00000    0.54    22.54     23.96

110.0 140.00000    6.27     8.52    736.04

5    4    6      16.608   140.0 140.00000    0.63     8.40     75.00

6    6    7       8.889   110.0 140.00000    1.39     8.53    163.00

125.0 140.00000    2.80     4.58    612.00

7    6    8       7.719    90.0 140.00000    1.70    17.46     97.38

110.0 140.00000   12.49     6.56   1902.62

============================================================================

Node Details

--------------

=============================================================================

Node    Peak Flow    Elevation    H G L    Cal Pres     Spc Pres   Meet Res

No.       (lps)        (m )        (m )      (m )         (m )    Pres. (Y)

-----------------------------------------------------------------------------

1 S       50.902      58.00      76.00      18.00         8.00

2          0.000      57.90      75.67      17.77         8.00

3 T      -25.405      65.00      73.00       8.00         8.00

4          0.000      50.00      68.82      18.82         8.00

5 T       -8.889      54.00      62.00       8.00         8.00

6          0.000      51.00      68.19      17.19         8.00

7 T       -8.889      56.00      64.00       8.00         8.00

8 T       -7.719      46.00      54.00       8.00         8.00

=============================================================================

Cost Summary

--------------

=================================================

Diameter    Length        Cost        Cum. Cost

(mm)        (m )      (1000 Rs )    (1000 Rs )

-------------------------------------------------

90.0      121.34         22.93         22.93

110.0     2801.66        756.45        779.38

125.0      612.00        212.36        991.75

140.0      138.80         59.96       1051.71

160.0      866.20        481.61       1533.31

225.0       50.00         50.20       1583.51

=================================================

Pipe-wise Cost Summary

------------------------

==========================================================

Pipe   Diameter      Length         Cost       Cum. Cost

No      (mm)        (m )       (1000 Rs )     (1000 Rs )

----------------------------------------------------------

1      225.0        50.00          50.20         50.20

2      140.0        63.80          27.56         77.76

160.0       156.20          86.85        164.61

3      160.0       710.00         394.76        559.37

4       90.0        23.96           4.53        563.90

110.0       736.04         198.73        762.63

5      140.0        75.00          32.40        795.03

6      110.0       163.00          44.01        839.04

125.0       612.00         212.36       1051.40

7       90.0        97.38          18.40       1069.81

110.0      1902.62         513.71       1583.51

ESR 18 – Chinchpada

| S.No. | village | Elevation |  | Population |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | Chinchpada | 128 | 480 | 600 | 800 |
| 2 | Devpada | 87 | 480 | 600 | 800 |
| 3 | Giripada | 118 | 480 | 600 | 800 |
| 4 | Umberwadi2 | 105 | 480 | 600 | 800 |
| 5 | Umberwadi1 | 103 | 480 | 600 | 800 |
| 6 | Banjarpada | 61 | 480 | 600 | 800 |
| 7 | Talwade Budruk | 57 | 480 | 600 | 800 |
|  | Total |  | 3360 | 4200 | 5600 |

| Daily Water Demand at 200 LPCD |
| --- |
| S.No. | village | Demand(MLD) | Demand(LPS) |
|  |  | 2011 | 2041 | 2011 | 2041 |
| 1 | Chinchpada | 0.115 | 0.192 | 5.333 | 8.889 |
| 2 | Devpada | 0.115 | 0.192 | 5.333 | 8.889 |
| 3 | Giripada | 0.115 | 0.192 | 5.333 | 8.889 |
| 4 | Umberwadi2 | 0.115 | 0.192 | 5.333 | 8.889 |
| 5 | Umberwadi1 | 0.115 | 0.192 | 5.333 | 8.889 |
| 6 | Banjarpada | 0.115 | 0.192 | 5.333 | 8.889 |
| 7 | Talwade Budruk | 0.115 | 0.192 | 5.333 | 8.889 |
|  | Total | 0.806 | 1.344 | 37.333 | 62.222 |

ESR 18 – Staging Height Optimization

| Total Demand | 1344000 |  |  |  |
| --- | --- | --- | --- | --- |
| ESR capacity Required | 504000 |  |  |  |
| ESR capacity Proposed | 504000 |  |  |  |
| Low level Height | 137 |  |  |  |
| ESR elevation | 128 |  |  |  |
| HGL | PIPE cost | ESR cost | Total | height |
| 139 | 3656.15 | 1862.715 | 5518.865 | 11 |
| 140 | 3580.82 | 1900.73 | 5481.55 | 12 |
| 141 | 3524.22 | 1938.745 | 5462.965 | 13 |
| 142 | 3470.12 | 1976.759 | 5446.879 | 14 |
| 143 | 3416.4 | 2014.774 | 5431.174 | 15 |
| 144 | 3377.79 | 2052.788 | 5430.578 | 16 |
| 145 | 3339.19 | 2109.81 | 5449 | 17 |
| 146 | 3300.57 | 2166.832 | 5467.402 | 18 |
| 147 | 3261.96 | 2223.854 | 5485.814 | 19 |
| 148 | 3223.35 | 2280.876 | 5504.226 | 20 |
| ESR capacity | 504000 |  |  |  |
| Optimum ESR height | 16 |  |  |  |
| ERS cost | 2052.79 |  |  |  |
| Pipe cost | 3377.79 |  |  |  |
| Total | 5430.58 |  |  |  |
| /person | 969.75 |  |  |  |

ESR 18 - BRANCH Input and Output

Echoing Input Variables

------------------------

Title of the Project                   :ESR 18

Name of the User                       :

Number of Pipes                        :  13

Number of Nodes                        :  14

Number of Commercial Diameters         :  16

Peak Design Factor                     :  1

Minimum Headloss in         m/km       :  .1

Maximum Headloss in         m/km       :  25

Minimum Residual Pressure   m          :  8

Type of Formula                        : Hazen's

Pipe Data

------------

===========================================================

Pipe  From   To     Length    Diameter  Hazen's   Status

No.  Node  Node      m         mm       Const    (E/P)

-----------------------------------------------------------

1    14     8       50.00

2     8     1      140.00

3     8     9     1300.00

4     9     2      100.00

5     9    10      650.00

6    10     3      270.00

7    10    11      500.00

8    11     4      520.00

9    11    12      420.00

10    12    13     1180.00

11    13     6      100.00

12    12     5      590.00

13    13     7      800.00

===========================================================

Node Data

-----------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

1   1.00      -8.889      128.00       8.00

2   1.00      -8.889       87.00       8.00

3   1.00      -8.889      118.00       8.00

4   1.00      -8.889      105.00       8.00

Node Data  cont`d

------------------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

5   1.00      -8.889      103.00       8.00

6   1.00      -8.889       61.00       8.00

7   1.00      -8.889       57.00       8.00

8   1.00       0.000      127.80       8.00

9   1.00       0.000       74.00       8.00

10   1.00       0.000      109.00       8.00

11   1.00       0.000      103.00       8.00

12   1.00       0.000      108.00       8.00

13   1.00       0.000       61.00       8.00

14   1.00       0.000      128.00       8.00

============================================================

Reference Node Data

---------------------

===================

Node   Grade Line

No.       m

-------------------

14      144.00

===================

Commercial Diameter Data

--------------------------

====================================

Pipe Dia.   Hazen's    Unit Cost

Int. (mm)   Const    Rs /m   length

------------------------------------

63.0   140.00000       98.00

75.0   140.00000      138.00

90.0   140.00000      189.00

110.0   140.00000      270.00

125.0   140.00000      347.00

140.0   140.00000      432.00

160.0   140.00000      556.00

180.0   140.00000      695.00

200.0   140.00000      789.00

225.0   140.00000     1004.00

250.0   140.00000     1228.00

280.0   140.00000     1532.00

315.0   140.00000     1932.00

355.0   140.00000     2210.00

Commercial Diameter Data  cont`d

---------------------------------

====================================

Pipe Dia.   Hazen's    Unit Cost

Int. (mm)   Const    Rs /m   length

------------------------------------

400.0   140.00000     3147.00

500.0   140.00000     4000.00

====================================

Branched Water Distribution Network Design OutPut

---------------------------------------------------

Pipe Details

--------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

1   14    8      62.223   225.0 140.00000    0.48     9.60     50.00

2    8    1       8.889    90.0 140.00000    3.17    22.64    140.00

3    8    9      53.334   200.0 140.00000    2.35    12.77    184.08

225.0 140.00000    8.02     7.19   1115.92

4    9    2       8.889    90.0 140.00000    2.26    22.60    100.00

5    9   10      44.445   200.0 140.00000    5.92     9.11    650.00

6   10    3       8.889   125.0 140.00000    1.23     4.56    270.00

7   10   11      35.556   180.0 140.00000    5.03    10.06    500.00

8   11    4       8.889    90.0 140.00000    7.65    22.65    337.77

110.0 140.00000    1.55     8.51    182.23

9   11   12      26.667   140.0 140.00000    3.70    20.11    184.00

160.0 140.00000    2.48    10.51    236.00

10   12   13      17.778   125.0 140.00000   19.45    16.48   1180.00

11   13    6       8.889    90.0 140.00000    2.26    22.60    100.00

12   12    5       8.889   110.0 140.00000    5.03     8.53    590.00

13   13    7       8.889    90.0 140.00000   18.12    22.65    800.00

============================================================================

Node Details

-------------- =============================================================================

Node    Peak Flow    Elevation    H G L    Cal Pres     Spc Pres   Meet Res

No.       (lps)        (m )        (m )      (m )         (m )    Pres. (Y)

-----------------------------------------------------------------------------

1 T       -8.889     128.00     140.35      12.35         8.00

2 T       -8.889      87.00     130.89      43.89         8.00

Node Details  cont`d

---------------------

=============================================================================

Node    Peak Flow    Elevation    H G L    Cal Pres     Spc Pres   Meet Res

No.       (lps)        (m )        (m )      (m )         (m )    Pres. (Y)

-----------------------------------------------------------------------------

3 T       -8.889     118.00     126.00       8.00         8.00

4 T       -8.889     105.00     113.00       8.00         8.00

5 T       -8.889     103.00     111.00       8.00         8.00

6 T       -8.889      61.00      94.31      33.31         8.00

7 T       -8.889      57.00      78.46      21.46         8.00

8          0.000     127.80     143.52      15.72         8.00

9          0.000      74.00     133.15      59.15         8.00

10          0.000     109.00     127.23      18.23         8.00

11          0.000     103.00     122.20      19.20         8.00

12          0.000     108.00     116.03       8.03         8.00

13          0.000      61.00      96.57      35.57         8.00

14 S       62.223     128.00     144.00      16.00         8.00

=============================================================================

Cost Summary

--------------

=================================================

Diameter    Length        Cost        Cum. Cost

(mm)        (m )      (1000 Rs )    (1000 Rs )

-------------------------------------------------

90.0     1477.77        279.30        279.30

110.0      772.23        208.50        487.80

125.0     1450.00        503.15        990.95

140.0      184.00         79.49       1070.44

160.0      236.00        131.21       1201.65

180.0      500.00        347.50       1549.15

200.0      834.08        658.09       2207.25

225.0     1165.92       1170.58       3377.83

=================================================

Pipe-wise Cost Summary

------------------------

==========================================================

Pipe   Diameter      Length         Cost       Cum. Cost

No      (mm)        (m )       (1000 Rs )     (1000 Rs )

----------------------------------------------------------

1      225.0        50.00          50.20         50.20

2       90.0       140.00          26.46         76.66

3      200.0       184.08         145.24        221.90

225.0      1115.92        1120.38       1342.28

4       90.0       100.00          18.90       1361.18

Pipe-wise Cost Summary  cont`d

-------------------------------

==========================================================

Pipe   Diameter      Length         Cost       Cum. Cost

No      (mm)        (m )       (1000 Rs )     (1000 Rs )

----------------------------------------------------------

5      200.0       650.00         512.85       1874.03

6      125.0       270.00          93.69       1967.72

7      180.0       500.00         347.50       2315.22

8       90.0       337.77          63.84       2379.06

110.0       182.23          49.20       2428.26

9      140.0       184.00          79.49       2507.75

160.0       236.00         131.22       2638.97

10      125.0      1180.00         409.46       3048.43

11       90.0       100.00          18.90       3067.33

12      110.0       590.00         159.30       3226.63

13       90.0       800.00         151.20       3377.83

ESR 19 – Kurung

| S.No. | village | Elevation |  | Population |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | Thakurwadi | 111 | 480 | 600 | 800 |
| 2 | Jambhulwadi | 106 | 480 | 600 | 800 |
| 3 | Haryachiwadi | 121 | 480 | 600 | 800 |
| 4 | Kurung | 96 | 650 | 765 | 899 |
|  | Total |  | 2090 | 2565 | 3299 |

| Daily Water Demand at 200 LPCD |
| --- |
| S.No. | village | Demand(MLD) | Demand(LPS) |
|  |  | 2011 | 2041 | 2011 | 2041 |
| 1 | Thakurwadi | 0.115 | 0.192 | 5.333 | 8.889 |
| 2 | Jambhulwadi | 0.115 | 0.192 | 5.333 | 8.889 |
| 3 | Haryachiwadi | 0.115 | 0.192 | 5.333 | 8.889 |
| 4 | Kurung | 0.156 | 0.216 | 7.219 | 9.993 |
|  | Total | 0.502 | 0.792 | 23.219 | 36.660 |

ESR 19 – Staging Height Optimization

| Total Demand | 791856 |  |  |  |
| --- | --- | --- | --- | --- |
| ESR capacity Required | 296946 |  |  |  |
| ESR capacity Proposed | 300000 |  |  |  |
| Low level Height | 130 |  |  |  |
| ESR elevation | 118 |  |  |  |
| HGL | PIPE cost | ESR cost | Total | height |
| 130 | 2213.02 | 1354.21 | 3567.23 | 12 |
| 131 | 2186.82 | 1381.294 | 3568.114 | 13 |
| 132 | 2152.68 | 1408.378 | 3561.058 | 14 |
| 133 | 2122.51 | 1435.463 | 3557.973 | 15 |
| 134 | 2092.35 | 1462.547 | 3554.897 | 16 |
| 135 | 2062.17 | 1503.173 | 3565.343 | 17 |
| 136 | 2031.99 | 1543.799 | 3575.789 | 18 |
| 137 | 2001.82 | 1584.426 | 3586.246 | 19 |
| 138 | 1971.65 | 1625.052 | 3596.702 | 20 |
| 139 | 1941.48 | 1679.22 | 3620.7 | 21 |
| 140 | 1911.31 | 1733.389 | 3644.699 | 22 |
| Optimum ESR height | 16 |  |  |  |
| ERS cost | 1462.55 |  |  |  |
| Pipe cost | 2092.35 |  |  |  |
| Total | 3554.90 |  |  |  |
| /person | 1077 |  |  |  |

ESR 19 - BRANCH Input and Output

Echoing Input Variables

------------------------

Title of the Project                   :ESR 19

Name of the User                       :

Number of Pipes                        :  7

Number of Nodes                        :  8

Number of Commercial Diameters         :  16

Peak Design Factor                     :  1

Minimum Headloss in         m/km       :  .1

Maximum Headloss in         m/km       :  25

Minimum Residual Pressure   m          :  8

Type of Formula                        : Hazen's

Pipe Data

------------

===========================================================

Pipe  From   To     Length    Diameter  Hazen's   Status

No.  Node  Node      m         mm       Const    (E/P)

-----------------------------------------------------------

1     1     2       50.00

2     2     3      260.00

3     3     4      100.00

4     3     5      950.00

5     2     6     2450.00

6     6     7      770.00

7     7     8      470.00

===========================================================

Node Data

-----------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

1   1.00       0.000      118.00       8.00

2   1.00       0.000      117.90       8.00

3   1.00       0.000      111.00       8.00

4   1.00      -8.889      111.00       8.00

5   1.00      -8.889      106.00       8.00

6   1.00       0.000       74.00       8.00

7   1.00      -8.889      121.00       8.00

8   1.00      -9.993       96.00       8.00

============================================================

Reference Node Data

---------------------

===================

Node   Grade Line

No.       m

-------------------

1      134.00

===================

Commercial Diameter Data

--------------------------

====================================

Pipe Dia.   Hazen's    Unit Cost

Int. (mm)   Const    Rs /m   length

------------------------------------

63.0   140.00000       98.00

75.0   140.00000      138.00

90.0   140.00000      189.00

110.0   140.00000      270.00

125.0   140.00000      347.00

140.0   140.00000      432.00

160.0   140.00000      556.00

180.0   140.00000      695.00

200.0   140.00000      789.00

225.0   140.00000     1004.00

250.0   140.00000     1228.00

280.0   140.00000     1532.00

315.0   140.00000     1932.00

355.0   140.00000     2210.00

400.0   140.00000     3147.00

500.0   140.00000     4000.00

====================================

Branched Water Distribution Network Design OutPut

---------------------------------------------------

Pipe Details

--------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

1    1    2      36.660   200.0 140.00000    0.32     6.40     50.00

2    2    3      17.778   125.0 140.00000    4.29    16.50    260.00

3    3    4       8.889    90.0 140.00000    2.26    22.60    100.00

Pipe Details  cont`d

---------------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

4    3    5       8.889    90.0 140.00000   11.70    22.64    516.74

110.0 140.00000    3.69     8.52    433.26

5    2    6      18.882   140.0 140.00000   19.20    10.62   1808.69

160.0 140.00000    3.55     5.54    641.31

6    6    7      18.882   160.0 140.00000    4.26     5.53    770.00

7    7    8       9.993   125.0 140.00000    2.67     5.68    470.00

============================================================================

Node Details

--------------

=============================================================================

Node    Peak Flow    Elevation    H G L    Cal Pres     Spc Pres   Meet Res

No.       (lps)        (m )        (m )      (m )         (m )    Pres. (Y)

-----------------------------------------------------------------------------

1 S       36.660     118.00     134.00      16.00         8.00

2          0.000     117.90     133.68      15.78         8.00

3          0.000     111.00     129.39      18.39         8.00

4 T       -8.889     111.00     127.13      16.13         8.00

5 T       -8.889     106.00     114.00       8.00         8.00

6          0.000      74.00     110.93      36.93         8.00

7         -8.889     121.00     106.67     -14.33 *       8.00

8 T       -9.993      96.00     104.00       8.00         8.00

=============================================================================

Cost Summary

--------------

=================================================

Diameter    Length        Cost        Cum. Cost

(mm)        (m )      (1000 Rs )    (1000 Rs )

-------------------------------------------------

90.0      616.74        116.56        116.56

110.0      433.26        116.98        233.54

125.0      730.00        253.31        486.85

140.0     1808.69        781.35       1268.21

160.0     1411.31        784.69       2052.90

200.0       50.00         39.45       2092.35

Pipe-wise Cost Summary

------------------------

==========================================================

Pipe   Diameter      Length         Cost       Cum. Cost

No      (mm)        (m )       (1000 Rs )     (1000 Rs )

----------------------------------------------------------

1      200.0        50.00          39.45         39.45

2      125.0       260.00          90.22        129.67

3       90.0       100.00          18.90        148.57

4       90.0       516.74          97.66        246.23

110.0       433.26         116.98        363.21

5      140.0      1808.69         781.35       1144.57

160.0       641.31         356.57       1501.14

6      160.0       770.00         428.12       1929.26

7      125.0       470.00         163.09       2092.35

ESR Profiles

for 40 LPCD Design

ESR 1 – Shilar

| S.No. | Village | Elevation | Population |
| --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | Shilar | 138 | 737 | 912 | 1126 |
| 2 | Unknown | 119 | 480 | 600 | 800 |
| 3 | Khadyrachiwadi | 133 | 480 | 600 | 800 |
| 4 | Kikur | 91 | 480 | 600 | 800 |
| 5 | Borwadi | 90 | 480 | 600 | 800 |
|  | Total |  | 2657 | 3312 | 4326 |

| Daily Water Demand at 40 lpcd 40LPCD |
| --- |
| S.No. | Village | Demand(MLD) | Demand(LPS) |
|  |  | 2011 | 2041 | 2011 | 2041 |
| 1 | Shilar | 0.128 | 0.208 | 5.904 | 9.613 |
| 2 | Unknown | 0.128 | 0.208 | 5.904 | 9.613 |
| 3 | Khadyrachiwadi | 0.128 | 0.208 | 5.904 | 9.613 |
| 4 | Kikur | 0.128 | 0.208 | 5.904 | 9.613 |
| 5 | Borwadi | 0.128 | 0.208 | 5.904 | 9.613 |
|  | Total | 0.128 | 0.208 | 5.904 | 9.613 |

ESR 1 – Staging Height Optimization

| Total Demand | 207648 |  |  |  |
| --- | --- | --- | --- | --- |
| ESR capacity Required | 77868 |  |  |  |
| ESR capacity Proposed | 78000 |  |  |  |
| Low level Height | 147 |  |  |  |
| ESR elevation | 135 |  |  |  |
| HGL | PIPE cost | ESR cost | Total | height |
| 147 | 493.74 | 586.925 | 1080.665 | 12 |
| 148 | 471.7 | 598.6635 | 1070.3635 | 13 |
| 149 | 461.56 | 610.402 | 1071.962 | 14 |
| 150 | 455.51 | 622.1405 | 1077.6505 | 15 |
| 151 | 455.51 | 633.879 | 1089.389 | 16 |
| 152 | 455.51 | 651.48675 | 1106.99675 | 17 |
| 153 | 455.51 | 669.0945 | 1124.6045 | 18 |
| 154 | 455.51 | 686.70225 | 1142.21225 | 19 |
| 155 | 455.51 | 704.31 | 1159.82 | 20 |
| 156 | 455.51 | 727.787 | 1183.297 | 21 |
| 157 | 455.51 | 751.264 | 1206.774 | 22 |
| 158 | 455.51 | 774.741 | 1230.251 | 23 |
| 159 | 455.51 | 798.218 | 1253.728 | 24 |
| 160 | 455.51 | 821.695 | 1277.205 | 25 |
| ESR capacity | 78000 |  |  |  |
| Optimum ESR height | 13 |  |  |  |
| ERS cost | 598.66 |  |  |  |
| Pipe cost | 471.70 |  |  |  |
| Total | 1070.36 |  |  |  |
| /person | 247 |  |  |  |

ESR 1 – Branch Output

Echoing Input Variables

------------------------

Title of the Project                   : ESR 1(40 LPCD)

Name of the User                       :

Number of Pipes                        :  9

Number of Nodes                        :  10

Number of Commercial Diameters         :  16

Peak Design Factor                     :  1

Minimum Headloss in         m/km       :  .1

Maximum Headloss in         m/km       :  25

Minimum Residual Pressure   m          :  8

Type of Formula                        : Hazen's

Pipe Data

------------

===========================================================

Pipe  From   To     Length    Diameter  Hazen's   Status

No.  Node  Node      m         mm       Const    (E/P)

-----------------------------------------------------------

1     1     2       50.00

2     2     3      200.00

3     3     4       50.00

4     3     5     2050.00

5     2     6      340.00

6     6     7       50.00

7     6     8     1400.00

8     8     9      100.00

9     8    10      100.00

===========================================================

Node Data

-----------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

1   1.00       0.000      135.00       8.00

2   1.00       0.000      134.90       8.00

3   1.00       0.000      133.00       8.00

4   1.00      -2.502      138.00       8.00

5   1.00      -1.778      119.00       8.00

6   1.00       0.000      133.00       8.00

7   1.00      -1.778      133.00       8.00

8   1.00       0.000       85.00       8.00

Node Data  cont`d

------------------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

9   1.00      -1.778       91.00       8.00

10   1.00      -1.778       90.00       8.00

============================================================

Reference Node Data

---------------------

===================

Node   Grade Line

No.       m

-------------------

1      148.00

===================

Commercial Diameter Data

--------------------------

====================================

Pipe Dia.   Hazen's    Unit Cost

Int. (mm)   Const    Rs /m   length

------------------------------------

63.0   140.00000       98.00

75.0   140.00000      138.00

90.0   140.00000      189.00

110.0   140.00000      270.00

125.0   140.00000      347.00

140.0   140.00000      432.00

160.0   140.00000      556.00

180.0   140.00000      695.00

200.0   140.00000      789.00

225.0   140.00000     1004.00

250.0   140.00000     1228.00

280.0   140.00000     1532.00

315.0   140.00000     1932.00

355.0   140.00000     2210.00

400.0   140.00000     3147.00

500.0   140.00000     4000.00

====================================

Branched Water Distribution Network Design OutPut

---------------------------------------------------

Pipe Details

--------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

1    1    2       9.614   110.0 140.00000    0.49     9.80     50.00

2    2    3       4.280    75.0 140.00000    0.12    13.97      8.59

90.0 140.00000    1.12     5.85    191.41

3    3    4       2.502    75.0 140.00000    0.26     5.20     50.00

4    3    5       1.778    63.0 140.00000   13.43     6.55   2050.00

5    2    6       5.334    75.0 140.00000    5.41    21.37    253.10

90.0 140.00000    0.77     8.86     86.90

6    6    7       1.778    63.0 140.00000    0.33     6.60     50.00

7    6    8       3.556    63.0 140.00000   33.07    23.62   1400.00

8    8    9       1.778    63.0 140.00000    0.66     6.60    100.00

9    8   10       1.778    63.0 140.00000    0.66     6.60    100.00

============================================================================

Node Details

--------------

=============================================================================

Node    Peak Flow    Elevation    H G L    Cal Pres     Spc Pres   Meet Res

No.       (lps)        (m )        (m )      (m )         (m )    Pres. (Y)

-----------------------------------------------------------------------------

1 S        9.614     135.00     148.00      13.00         8.00

2          0.000     134.90     147.51      12.61         8.00

3          0.000     133.00     146.26      13.26         8.00

4 T       -2.502     138.00     146.00       8.00         8.00

5 T       -1.778     119.00     132.83      13.83         8.00

6          0.000     133.00     141.33       8.33         8.00

7 T       -1.778     133.00     141.00       8.00         8.00

8          0.000      85.00     108.26      23.26         8.00

9 T       -1.778      91.00     107.60      16.60         8.00

10 T       -1.778      90.00     107.60      17.60         8.00

=============================================================================

Cost Summary

--------------

=================================================

Diameter    Length        Cost        Cum. Cost

(mm)        (m )      (1000 Rs )    (1000 Rs )

-------------------------------------------------

63.0     3700.00        362.60        362.60

75.0      311.69         43.01        405.61

90.0      278.31         52.60        458.21

110.0       50.00         13.50        471.71

=================================================

Pipe-wise Cost Summary

------------------------

==========================================================

Pipe   Diameter      Length         Cost       Cum. Cost

No      (mm)        (m )       (1000 Rs )     (1000 Rs )

----------------------------------------------------------

1      110.0        50.00          13.50         13.50

2       75.0         8.59           1.19         14.69

90.0       191.41          36.18         50.86

3       75.0        50.00           6.90         57.76

4       63.0      2050.00         200.90        258.66

5       75.0       253.10          34.93        293.59

90.0        86.90          16.42        310.01

6       63.0        50.00           4.90        314.91

7       63.0      1400.00         137.20        452.11

8       63.0       100.00           9.80        461.91

9       63.0       100.00           9.80        471.71

ESR 2 – Pathraj

| S.No. | Village | Elevation (m) |  | Population |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | Pathraj | 150 | 2058 | 2402 | 2773 |
| 2 | Nagyachiwadi | 158 | 480 | 600 | 800 |
|  | Total |  | 2538 | 3002 | 3573 |

| Daily Water Demand at 40 lpcd 40 lpcd |
| --- |
| S.No. | Village | Demand(MLD) | Demand(LPS) |
|  |  | 2011 | 2041 | 2011 | 2041 |
| 1 | Pathraj | 0.099 | 0.133 | 4.573 | 6.162 |
| 2 | Nagyachiwadi | 0.023 | 0.038 | 1.067 | 1.778 |
|  | Total | 0.122 | 0.172 | 5.640 | 7.940 |

ESR 2 – Staging Height Optimization

| Total Demand | 171504 |  |  |  |
| --- | --- | --- | --- | --- |
| ESR capacity Required | 64314 |  |  |  |
| ESR capacity Proposed | 65000 |  |  |  |
| Low level Height | 172 |  |  |  |
| ESR elevation | 164 |  |  |  |
| HGL | PIPE cost | ESR cost | Total | height |
| 172 | 263.84 | 477.2362 | 741.0762 | 8 |
| 173 | 253.17 | 487.6109 | 740.7809 | 9 |
| 174 | 242.5 | 497.9856 | 740.4856 | 10 |
| 175 | 231.83 | 508.3603 | 740.1903 | 11 |
| 176 | 222.9 | 518.735 | 741.635 | 12 |
| 177 | 222.25 | 529.1097 | 751.3597 | 13 |
| 178 | 222.25 | 539.4844 | 761.7344 | 14 |
| 179 | 222.25 | 549.8591 | 772.1091 | 15 |
| 180 | 222.25 | 560.2338 | 782.4838 | 16 |
| ESR capacity | 322000 |  |  |  |
| Optimum ESR height | 11 |  |  |  |
| ERS cost | 508.36 |  |  |  |
| Pipe cost | 231.83 |  |  |  |
| Total | 740.19 |  |  |  |
| /person | 207.162133 |  |  |  |

ESR 2 - BRANCH Input and Output

Echoing Input Variables

------------------------

Title of the Project                   : ESR 2(40 LPCD)

Name of the User                       :

Number of Pipes                        :  3

Number of Nodes                        :  4

Number of Commercial Diameters         :  15

Peak Design Factor                     :  1

Minimum Headloss in         m/km       :  .1

Maximum Headloss in         m/km       :  25

Minimum Residual Pressure   m          :  8

Type of Formula                        : Hazen's

Pipe Data

------------

===========================================================

Pipe  From   To     Length    Diameter  Hazen's   Status

No.  Node  Node      m         mm       Const    (E/P)

-----------------------------------------------------------

1     1     2       50.00

2     2     3      400.00

3     2     4     1400.00

===========================================================

Node Data

-----------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

1   1.00       0.000      164.00       8.00

2   1.00       0.000      163.90       8.00

3   1.00      -6.162      150.00       8.00

4   1.00      -1.778      158.00       8.00

============================================================

Reference Node Data

---------------------

===================

Node   Grade Line

No.       m

-------------------

1      175.00

===================

Commercial Diameter Data

--------------------------

====================================

Pipe Dia.   Hazen's    Unit Cost

Int. (mm)   Const    Rs /m   length

------------------------------------

63.0   140.00000       98.00

75.0   140.00000      138.00

90.0   140.00000      189.00

110.0   140.00000      270.00

125.0   140.00000      347.00

140.0   140.00000      432.00

160.0   140.00000      556.00

180.0   140.00000      695.00

200.0   140.00000      789.00

225.0   140.00000     1004.00

250.0   140.00000     1228.00

280.0   140.00000     1532.00

315.0   140.00000     1932.00

355.0   140.00000     2215.00

400.0   140.00000     3147.00

====================================

Branched Water Distribution Network Design OutPut

Pipe Details

--------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

1    1    2       7.940   110.0 140.00000    0.35     7.00     50.00

2    2    3       6.162    90.0 140.00000    4.60    11.50    400.00

3    2    4       1.778    63.0 140.00000    8.27     6.55   1261.69

75.0 140.00000    0.39     2.82    138.31

============================================================================

Node Details

--------------

=============================================================================

Node    Peak Flow    Elevation    H G L    Cal Pres     Spc Pres   Meet Res

No.       (lps)        (m )        (m )      (m )         (m )    Pres. (Y)

-----------------------------------------------------------------------------

1 S        7.940     164.00     175.00      11.00         8.00

2          0.000     163.90     174.65      10.75         8.00

3 T       -6.162     150.00     170.06      20.06         8.00

4 T       -1.778     158.00     166.00       8.00         8.00

=============================================================================

Cost Summary

--------------

=================================================

Diameter    Length        Cost        Cum. Cost

(mm)        (m )      (1000 Rs )    (1000 Rs )

-------------------------------------------------

63.0     1261.69        123.65        123.65

75.0      138.31         19.09        142.73

90.0      400.00         75.60        218.33

110.0       50.00         13.50        231.83

=================================================

Pipe-wise Cost Summary

------------------------

==========================================================

Pipe   Diameter      Length         Cost       Cum. Cost

No      (mm)        (m )       (1000 Rs )     (1000 Rs )

----------------------------------------------------------

1      110.0        50.00          13.50         13.50

2       90.0       400.00          75.60         89.10

3       63.0      1261.69         123.65        212.75

75.0       138.31          19.09        231.83

ESR 3 – Tadwadi

| S.No. | Village | Elevation |  | Population |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | Morachiwadi | 151 | 480 | 600 | 800 |
| 2 | Tadwadi | 144 | 827 | 985 | 1166 |
| 3 | Margachiwadi | 138 | 425 | 577 | 773 |
| 4 | Jambhulwadi | 137 | 480 | 600 | 800 |
| 5 | Jalkatwadi | 150 | 480 | 600 | 800 |
| 6 | Dongarpada | 165 | 480 | 600 | 800 |
|  | Total |  | 3172 | 3962 | 5139 |

| Daily Water Demand at 40 lpcd 40 lpcd |
| --- |
|  |  | Demand(MLD) | Demand(LPS) |
| S.No. | Village | 2011 | 2041 | 2011 | 2041 |
| 1 | Morachiwadi | 0.023 | 0.038 | 1.067 | 1.778 |
| 2 | Tadwadi | 0.040 | 0.056 | 1.838 | 2.591 |
| 3 | Margachiwadi | 0.020 | 0.037 | 0.944 | 1.718 |
| 4 | Jambhulwadi | 0.023 | 0.038 | 1.067 | 1.778 |
| 5 | Jalkatwadi | 0.023 | 0.038 | 1.067 | 1.778 |
| 6 | Dongarpada | 0.023 | 0.038 | 1.067 | 1.778 |
|  | Total | 0.152 | 0.247 | 7.049 | 11.420 |

ESR 3 – Staging Height Optimization

| Total Demand | 246672 |  |  |  |
| --- | --- | --- | --- | --- |
| ESR capacity Required | 92502 |  |  |  |
| ESR capacity Proposed | 93000 |  |  |  |
| Low level Height | 174 |  |  |  |
| ESR elevation | 165 |  |  |  |
| HGL | PIPE cost | ESR cost | Total | height |
| 176 | 753.6 | 645.4525 | 1399.053 | 11 |
| 177 | 715.75 | 658.625 | 1374.375 | 12 |
| 178 | 684.83 | 671.7975 | 1356.628 | 13 |
| 179 | 653.91 | 684.97 | 1338.88 | 14 |
| 180 | 624.02 | 698.1425 | 1322.163 | 15 |
| 181 | 609.34 | 711.315 | 1320.655 | 16 |
| 182 | 598.68 | 731.0738 | 1329.754 | 17 |
| 183 | 588.01 | 750.8325 | 1338.843 | 18 |
| 184 | 577.34 | 770.5913 | 1347.931 | 19 |
| 185 | 566.67 | 790.35 | 1357.02 | 20 |
| ESR capacity | 463000 |  |  |  |
| Optimum ESR height | 16 |  |  |  |
| ERS cost | 711.32 |  |  |  |
| Pipe cost | 609.34 |  |  |  |
| Total | 1320.66 |  |  |  |
| /person | 256.986768 |  |  |  |

ESR 3 - BRANCH Input and Output

Echoing Input Variables

------------------------

Title of the Project                   :ESR  3

Name of the User                       :

Number of Pipes                        :  11

Number of Nodes                        :  12

Number of Commercial Diameters         :  15

Peak Design Factor                     :  1

Minimum Headloss in         m/km       :  .1

Maximum Headloss in         m/km       :  25

Minimum Residual Pressure   m          :  8

Type of Formula                        : Hazen's

Pipe Data

------------

===========================================================

Pipe  From   To     Length    Diameter  Hazen's   Status

No.  Node  Node      m         mm       Const    (E/P)

-----------------------------------------------------------

1     1     2      100.00

2     2     3      680.00

3     3     4       80.00

4     3     5      840.00

5     2     6      230.00

6     6     7      105.00

7     6     8      300.00

8     6     9      105.00

9     9    10      465.00

11     9    12      380.00

12    12    11     1310.00

===========================================================

Node Data

-----------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

1   1.00       0.000      165.00       8.00

2   1.00       0.000      161.00       8.00

3   1.00       0.000      151.00       8.00

4   1.00      -1.778      151.00       8.00

5   1.00      -2.591      144.00       8.00

6   1.00       0.000      135.00       8.00

Node Data  cont`d

------------------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

7   1.00      -1.718      138.00       8.00

8   1.00      -1.778      137.00       8.00

9   1.00       0.000      134.00       8.00

10   1.00      -1.778      150.00       8.00

11   1.00      -1.778      165.00       8.00

12   1.00       0.000      127.00       8.00

============================================================

Reference Node Data

---------------------

===================

Node   Grade Line

No.       m

-------------------

1      181.00

===================

Commercial Diameter Data

--------------------------

====================================

Pipe Dia.   Hazen's    Unit Cost

Int. (mm)   Const    Rs /m   length

------------------------------------

63.0   140.00000       98.00

75.0   140.00000      138.00

90.0   140.00000      189.00

110.0   140.00000      270.00

125.0   140.00000      347.00

140.0   140.00000      432.00

160.0   140.00000      556.00

180.0   140.00000      695.00

200.0   140.00000      789.00

225.0   140.00000     1004.00

250.0   140.00000     1228.00

280.0   140.00000     1532.00

315.0   140.00000     1932.00

355.0   140.00000     2215.00

400.0   140.00000     3147.00

====================================

Branched Water Distribution Network Design OutPut

---------------------------------------------------

Pipe Details

--------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

1    1    2      11.421   110.0 140.00000    1.36    13.60    100.00

2    2    3       4.369    75.0 140.00000   10.06    14.79    680.00

3    3    4       1.778    63.0 140.00000    0.52     6.50     80.00

4    3    5       2.591    63.0 140.00000   11.05    13.15    840.00

5    2    6       7.052   110.0 140.00000    1.28     5.57    230.00

6    6    7       1.718    63.0 140.00000    0.65     6.19    105.00

7    6    8       1.778    63.0 140.00000    1.97     6.57    300.00

8    6    9       3.556    90.0 140.00000    0.44     4.19    105.00

9    9   10       1.778    63.0 140.00000    3.05     6.56    465.00

11    9   12       1.778    75.0 140.00000    1.07     2.82    380.00

12   12   11       1.778    63.0 140.00000    0.34     6.57     51.77

75.0 140.00000    3.53     2.81   1258.23

============================================================================

Node Details

--------------

=============================================================================

Node    Peak Flow    Elevation    H G L    Cal Pres     Spc Pres   Meet Res

No.       (lps)        (m )        (m )      (m )         (m )    Pres. (Y)

-----------------------------------------------------------------------------

1 S       11.421     165.00     181.00      16.00         8.00

2          0.000     161.00     179.64      18.64         8.00

3          0.000     151.00     169.59      18.59         8.00

4 T       -1.778     151.00     169.06      18.06         8.00

5 T       -2.591     144.00     158.54      14.54         8.00

6          0.000     135.00     178.37      43.37         8.00

7 T       -1.718     138.00     177.72      39.72         8.00

8 T       -1.778     137.00     176.40      39.40         8.00

9          0.000     134.00     177.93      43.93         8.00

10 T       -1.778     150.00     174.88      24.88         8.00

11 T       -1.778     165.00     173.00       8.00         8.00

12          0.000     127.00     176.87      49.87         8.00

=============================================================================

Cost Summary

--------------

=================================================

Diameter    Length        Cost        Cum. Cost

(mm)        (m )      (1000 Rs )    (1000 Rs )

-------------------------------------------------

63.0     1841.77        180.49        180.49

75.0     2318.23        319.92        500.41

90.0      105.00         19.84        520.25

110.0      330.00         89.10        609.35

=================================================

Pipe-wise Cost Summary

------------------------

==========================================================

Pipe   Diameter      Length         Cost       Cum. Cost

No      (mm)        (m )       (1000 Rs )     (1000 Rs )

----------------------------------------------------------

1      110.0       100.00          27.00         27.00

2       75.0       680.00          93.84        120.84

3       63.0        80.00           7.84        128.68

4       63.0       840.00          82.32        211.00

5      110.0       230.00          62.10        273.10

6       63.0       105.00          10.29        283.39

7       63.0       300.00          29.40        312.79

8       90.0       105.00          19.84        332.64

9       63.0       465.00          45.57        378.20

11       75.0       380.00          52.44        430.64

12       63.0        51.77           5.07        435.72

75.0      1258.23         173.64        609.35

ESR 4 – Bangarwadi

|  |  |  | Population |
| --- | --- | --- | --- |
| S.No. | Village | Elevation | 2011 | 2026 | 2041 |
| 1 | Bhangarwadi | 159 | 480 | 600 | 800 |
| 2 | Dhabewadi | 161 | 480 | 600 | 800 |
| 3 | Govanwadi | 123 | 480 | 600 | 800 |
| 4 | Petarwadi | 136 | 480 | 600 | 800 |
| 5 | Ghutewadi | 121 | 480 | 600 | 800 |
|  | Total |  | 2400 | 3000 | 4000 |

| Daily Water Demand at 40 lpcd |
| --- |
| S.No. | Village | Demand(MLD) | Demand(LPS) |
|  |  | 2011 | 2041 | 2011 | 2041 |
| 1 | Bhangarwadi | 0.023 | 0.038 | 1.067 | 1.778 |
| 2 | Dhabewadi | 0.023 | 0.038 | 1.067 | 1.778 |
| 3 | Govanwadi | 0.023 | 0.038 | 1.067 | 1.778 |
| 4 | Petarwadi | 0.023 | 0.038 | 1.067 | 1.778 |
| 5 | Ghutewadi | 0.023 | 0.038 | 1.067 | 1.778 |
|  | Total | 0.115 | 0.192 | 5.333 | 8.889 |

ESR 4 – Staging Height Optimization

| Total Demand | 192000 |  |  |  |
| --- | --- | --- | --- | --- |
| ESR capacity Required | 72000 |  |  |  |
| ESR capacity Proposed | 72000 |  |  |  |
| Low level Height | 184 |  |  |  |
| ESR elevation | 182 |  |  |  |
| HGL | PIPE cost | ESR cost | Total | height |
| 184 | 698.55 | 400.6044 | 1099.154 | 2 |
| 185 | 692.64 | 422.8602 | 1115.5 | 3 |
| 186 | 686.71 | 445.116 | 1131.826 | 4 |
| 187 | 680.8 | 461.8079 | 1142.608 | 5 |
| 188 | 674.88 | 478.4997 | 1153.38 | 6 |
| 189 | 669.87 | 495.1916 | 1165.062 | 7 |
| 190 | 663.34 | 511.8834 | 1175.223 | 8 |
| 191 | 657.6 | 523.0113 | 1180.611 | 9 |
| ESR capacity | 72000 |  |  |  |
| Optimum ESR height | 2 |  |  |  |
| ERS cost | 400.60 |  |  |  |
| Pipe cost | 698.55 |  |  |  |
| Total | 1099.15 |  |  |  |
| /person | 274.7886 |  |  |  |

ESR 4 - BRANCH Input and Output

Echoing Input Variables

------------------------

Title of the Project                   : ESR 4(40 LPCD)

Name of the User                       :

Number of Pipes                        :  9

Number of Nodes                        :  10

Number of Commercial Diameters         :  15

Peak Design Factor                     :  1

Minimum Headloss in         m/km       :  .1

Maximum Headloss in         m/km       :  25

Minimum Residual Pressure   m          :  8

Type of Formula                        : Hazen's

Pipe Data

------------

===========================================================

Pipe  From   To     Length    Diameter  Hazen's   Status

No.  Node  Node      m         mm       Const    (E/P)

-----------------------------------------------------------

1     1     2      200.00

2     2     3      520.00

3     3     4      150.00

4     3     5      830.00

5     2     6      500.00

6     6     7     1360.00

7     6     8     1400.00

8     8     9      500.00

9     8    10      715.00

===========================================================

Node Data

-----------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

1   1.00       0.000      182.00       8.00

2   1.00       0.000      175.00       8.00

3   1.00       0.000      157.00       8.00

4   1.00      -1.778      159.00       8.00

5   1.00      -1.778      161.00       8.00

6   1.00       0.000      160.00       8.00

7   1.00      -1.778      123.00       8.00

8   1.00       0.000      137.00       8.00

Node Data  cont`d

------------------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

9   1.00      -1.778      136.00       8.00

10   1.00      -1.778      121.00       8.00

============================================================

Reference Node Data

---------------------

===================

Node   Grade Line

No.       m

-------------------

1      184.00

===================

Commercial Diameter Data

--------------------------

====================================

Pipe Dia.   Hazen's    Unit Cost

Int. (mm)   Const    Rs /m   length

------------------------------------

63.0   140.00000       98.00

75.0   140.00000      138.00

90.0   140.00000      189.00

110.0   140.00000      270.00

125.0   140.00000      347.00

140.0   140.00000      432.00

160.0   140.00000      556.00

180.0   140.00000      695.00

200.0   140.00000      789.00

225.0   140.00000     1004.00

250.0   140.00000     1228.00

280.0   140.00000     1532.00

315.0   140.00000     1932.00

355.0   140.00000     2215.00

400.0   140.00000     3147.00

====================================

Branched Water Distribution Network Design OutPut

---------------------------------------------------

Pipe Details

--------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

1    1    2       8.890   110.0 140.00000    1.70     8.50    200.00

2    2    3       3.556    63.0 140.00000    4.55    23.63    192.57

75.0 140.00000    3.31    10.11    327.43

3    3    4       1.778    63.0 140.00000    0.98     6.53    150.00

4    3    5       1.778    63.0 140.00000    5.44     6.55    830.00

5    2    6       5.334    75.0 140.00000   10.70    21.40    500.00

6    6    7       1.778    63.0 140.00000    8.91     6.55   1360.00

7    6    8       3.556    63.0 140.00000   17.78    23.61    752.93

75.0 140.00000    6.54    10.11    647.07

8    8    9       1.778    63.0 140.00000    3.28     6.56    500.00

9    8   10       1.778    63.0 140.00000    4.68     6.55    715.00

============================================================================

Node Details

--------------

=============================================================================

Node    Peak Flow    Elevation    H G L    Cal Pres     Spc Pres   Meet Res

No.       (lps)        (m )        (m )      (m )         (m )    Pres. (Y)

-----------------------------------------------------------------------------

1 S        8.890     182.00     184.00       2.00         8.00

2          0.000     175.00     182.30       7.30 *       8.00

3          0.000     157.00     174.44      17.44         8.00

4 T       -1.778     159.00     173.46      14.46         8.00

5 T       -1.778     161.00     169.00       8.00         8.00

6          0.000     160.00     171.60      11.60         8.00

7 T       -1.778     123.00     162.69      39.69         8.00

8          0.000     137.00     147.28      10.28         8.00

9 T       -1.778     136.00     144.00       8.00         8.00

10 T       -1.778     121.00     142.59      21.59         8.00

=============================================================================

Cost Summary

--------------

=================================================

Diameter    Length        Cost        Cum. Cost

(mm)        (m )      (1000 Rs )    (1000 Rs )

-------------------------------------------------

63.0     4500.50        441.05        441.05

75.0     1474.50        203.48        644.53

110.0      200.00         54.00        698.53

=================================================

Pipe-wise Cost Summary

------------------------

==========================================================

Pipe   Diameter      Length         Cost       Cum. Cost

No      (mm)        (m )       (1000 Rs )     (1000 Rs )

----------------------------------------------------------

1      110.0       200.00          54.00         54.00

2       63.0       192.57          18.87         72.87

75.0       327.43          45.19        118.06

3       63.0       150.00          14.70        132.76

4       63.0       830.00          81.34        214.10

5       75.0       500.00          69.00        283.10

6       63.0      1360.00         133.28        416.38

7       63.0       752.93          73.79        490.16

75.0       647.07          89.30        579.46

8       63.0       500.00          49.00        628.46

9       63.0       715.00          70.07        698.53

ESR 5 – Khandas

| S.No. | Village | Elevation |  | Population |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | Belachiwadi | 174 | 480 | 600 | 800 |
| 2 | Amberpada | 166 | 480 | 600 | 800 |
| 3 | Katewadi | 163 | 480 | 600 | 800 |
| 4 | Khandas | 166 | 2637 | 2947 | 3285 |
|  | Total |  | 4077 | 4747 | 5685 |

| Daily Water Demand at 40 lpcd |
| --- |
| S.No. | village | Demand(MLD) | Demand(LPS) |
|  |  | 2011 | 2041 | 2011 | 2041 |
| 1 | Belachiwadi | 0.023 | 0.038 | 1.067 | 1.778 |
| 2 | Amberpada | 0.023 | 0.038 | 1.067 | 1.778 |
| 3 | Katewadi | 0.023 | 0.038 | 1.067 | 1.778 |
| 4 | Khandas | 0.127 | 0.158 | 5.860 | 7.300 |
|  | Total | 0.196 | 0.273 | 9.060 | 12.633 |

ESR 5 – Staging Height Optimization

| Total Demand | 272880 |  |  |  |
| --- | --- | --- | --- | --- |
| ESR capacity | 103000 |  |  |  |
| Low level Height | 183 |  |  |  |
| esr elevation | 174 |  |  |  |
| HGL | PIPE cost | ESR cost | Total | height |
| 189 | 1415.69 | 745.7047 | 2161.395 | 15 |
| 190 | 1364.39 | 759.7746 | 2124.165 | 16 |
| 191 | 1316.59 | 780.8795 | 2097.469 | 17 |
| 192 | 1281.58 | 801.9843 | 2083.564 | 18 |
| 193 | 1258.72 | 823.0892 | 2081.809 | 19 |
| 194 | 1235.86 | 844.194 | 2080.054 | 20 |
| 195 | 1215.4 | 872.3338 | 2087.734 | 21 |
| 196 | 1198.56 | 900.4736 | 2099.034 | 22 |
| 197 | 1181.73 | 928.6134 | 2110.343 | 23 |
| ESR capacity | 103000 |  |  |  |
| Esr height | 20 |  |  |  |
| esr cost | 844.194 |  |  |  |
| pipe cost | 1235.86 |  |  |  |
| total | 2080.054 |  |  |  |
| /Person cost | 365.8846 |  |  |  |

ESR 5 - BRANCH Input and Output

Echoing Input Variables

------------------------

Title of the Project                   : ESR 5(40 LPCD)

Name of the User                       :

Number of Pipes                        :  8

Number of Nodes                        :  9

Number of Commercial Diameters         :  16

Peak Design Factor                     :  1

Minimum Headloss in         m/km       :  .1

Maximum Headloss in         m/km       :  25

Minimum Residual Pressure   m          :  8

Type of Formula                        : Hazen's

Pipe Data

------------

===========================================================

Pipe  From   To     Length    Diameter  Hazen's   Status

No.  Node  Node      m         mm       Const    (E/P)

-----------------------------------------------------------

1     5     6      750.00

2     6     7     2080.00

3     7     8     1390.00

4     8     9      950.00

5     6     4      100.00

6     7     3      100.00

7     8     1       60.00

8     9     2      100.00

===========================================================

Node Data

-----------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

1   1.00      -1.778      174.00       8.00

2   1.00      -1.778      166.00       8.00

3   1.00      -1.778      163.00       8.00

4   1.00      -7.300      166.00       8.00

6   1.00       0.000      166.00       8.00

7   1.00       0.000      163.00       8.00

8   1.00       0.000      174.00       8.00

9   1.00       0.000      166.00       8.00

5   1.00       0.000      174.00       8.00

============================================================

Reference Node Data

---------------------

===================

Node   Grade Line

No.       m

-------------------

5      194.00

===================

Commercial Diameter Data

--------------------------

====================================

Pipe Dia.   Hazen's    Unit Cost

Int. (mm)   Const    Rs /m   length

------------------------------------

63.0   140.00000       98.00

75.0   140.00000      138.00

90.0   140.00000      189.00

110.0   140.00000      270.00

125.0   140.00000      347.00

140.0   140.00000      432.00

160.0   140.00000      556.00

180.0   140.00000      695.00

200.0   140.00000      789.00

225.0   140.00000     1004.00

250.0   140.00000     1228.00

280.0   140.00000     1532.00

315.0   140.00000     1932.00

355.0   140.00000     2210.00

400.0   140.00000     3147.00

500.0   140.00000     4000.00

====================================

Branched Water Distribution Network Design OutPut

---------------------------------------------------

Pipe Details

--------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

1    5    7      12.634   125.0 140.00000    5.34     8.76    609.91

140.0 140.00000    0.71     5.07    140.09

2    7    6       7.300    90.0 140.00000    0.10    16.21      6.17

Pipe Details  cont`d

---------------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

110.0 140.00000   12.28     5.92   2073.83

3    7    8       3.556    90.0 140.00000    5.78     4.16   1390.00

4    8    9       1.778    63.0 140.00000    6.22     6.55    950.00

5    6    4       7.300    90.0 140.00000    1.57    15.70    100.00

6    7    3       1.778    63.0 140.00000    0.66     6.60    100.00

7    8    1       1.778    75.0 140.00000    0.17     2.83     60.00

8    9    2       1.778    63.0 140.00000    0.66     6.60    100.00

============================================================================

Node Details

--------------

=============================================================================

Node    Peak Flow    Elevation    H G L    Cal Pres     Spc Pres   Meet Res

No.       (lps)        (m )        (m )      (m )         (m )    Pres. (Y)

-----------------------------------------------------------------------------

1 T       -1.778     174.00     182.00       8.00         8.00

2 T       -1.778     166.00     175.29       9.29         8.00

3 T       -1.778     163.00     187.29      24.29         8.00

4 T       -7.300     166.00     174.00       8.00         8.00

6          0.000     166.00     175.57       9.57         8.00

7          0.000     163.00     187.95      24.95         8.00

8          0.000     174.00     182.17       8.17         8.00

9          0.000     166.00     175.94       9.94         8.00

5 S       12.634     174.00     194.00      20.00         8.00

=============================================================================

Cost Summary

--------------

=================================================

Diameter    Length        Cost        Cum. Cost

(mm)        (m )      (1000 Rs )    (1000 Rs )

-------------------------------------------------

63.0     1150.00        112.70        112.70

75.0       60.00          8.28        120.98

90.0     1496.17        282.78        403.76

110.0     2073.83        559.93        963.69

125.0      609.91        211.64       1175.33

140.0      140.09         60.52       1235.85

=================================================

Pipe-wise Cost Summary

------------------------

==========================================================

Pipe   Diameter      Length         Cost       Cum. Cost

No      (mm)        (m )       (1000 Rs )     (1000 Rs )

----------------------------------------------------------

1      125.0       609.91         211.64        211.64

140.0       140.09          60.52        272.16

2       90.0         6.17           1.17        273.32

110.0      2073.83         559.93        833.26

3       90.0      1390.00         262.71       1095.97

4       63.0       950.00          93.10       1189.07

5       90.0       100.00          18.90       1207.97

6       63.0       100.00           9.80       1217.77

7       75.0        60.00           8.28       1226.05

8       63.0       100.00           9.80       1235.85

ESR 6 – Mangalwadi

| S.No. | Village | Elevation |  | Population |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | Mangal | 122 | 480 | 600 | 800 |
| 2 | Chafewadi | 129 | 1418 | 2117 | 3207 |
| 3 | Unknown | 113 | 480 | 600 | 800 |
| 4 | Jamhaiwadi | 133 | 480 | 600 | 800 |
|  | Total |  | 2858 | 3917 | 5607 |

| Daily Water Demand at 40 lpcd |
| --- |
| S.No. | village | Demand(MLD) | Demand(LPS) |
|  |  | 2011 | 2041 | 2011 | 2041 |
| 1 | Mangal | 0.023 | 0.038 | 1.067 | 1.778 |
| 2 | Chafewadi | 0.068 | 0.154 | 3.151 | 7.127 |
| 3 | Unknown | 0.023 | 0.038 | 1.067 | 1.778 |
| 4 | Jamhaiwadi | 0.023 | 0.038 | 1.067 | 1.778 |
|  | Total | 0.137 | 0.269 | 6.351 | 12.460 |

ESR 6 – Staging Height Optimization

| Total Demand | 269136 |  |  |  |
| --- | --- | --- | --- | --- |
| ESR capacity Required | 100926 |  |  |  |
| ESR capacity Proposed | 101000 |  |  |  |
| Low level Height | 142 |  |  |  |
| ESR elevation | 126 |  |  |  |
| HGL | PIPE cost | ESR cost | Total | height |
| 142 | 868.1 | 751.6314 | 1619.731 | 16 |
| 143 | 738.3 | 772.5101 | 1510.81 | 17 |
| 144 | 687.6 | 793.3887 | 1480.989 | 18 |
| 145 | 637.26 | 814.2674 | 1451.527 | 19 |
| 146 | 596.74 | 835.146 | 1431.886 | 20 |
| 147 | 571.18 | 862.9842 | 1434.164 | 21 |
| 148 | 551.88 | 890.8224 | 1442.702 | 22 |
| 149 | 533.01 | 918.6606 | 1451.671 | 23 |
| 150 | 516.63 | 946.4988 | 1463.129 | 24 |
| ESR capacity | 101000 |  |  |  |
| Optimum ESR height | 20 |  |  |  |
| ERS cost | 835.15 |  |  |  |
| Pipe cost | 596.74 |  |  |  |
| Total | 1431.89 |  |  |  |
| /person | 255.37471 |  |  |  |

ESR 6 - BRANCH Input and Output

Echoing Input Variables

------------------------

Title of the Project                   : ESR 6(40 LPCD)

Name of the User                       :

Number of Pipes                        :  8

Number of Nodes                        :  9

Number of Commercial Diameters         :  15

Peak Design Factor                     :  1

Minimum Headloss in         m/km       :  .1

Maximum Headloss in         m/km       :  25

Minimum Residual Pressure   m          :  8

Type of Formula                        : Hazen's

Pipe Data

------------

===========================================================

Pipe  From   To     Length    Diameter  Hazen's   Status

No.  Node  Node      m         mm       Const    (E/P)

-----------------------------------------------------------

1     1     2      100.00

2     2    10       60.00

3    10     3       50.00

4    10     4      850.00

5     4     5      200.00

6     4     6      470.00

7     2     7      635.00

8     7     8      800.00

===========================================================

Node Data

-----------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

1   1.00       0.000      126.00       8.00

2   1.00       0.000      125.90       8.00

3   1.00      -1.778      122.00       8.00

4   1.00       0.000      126.00       8.00

5   1.00      -7.127      129.00       8.00

6   1.00      -1.778      113.00       8.00

7   1.00       0.000       99.00       8.00

8   1.00      -1.778      133.00       8.00

10   1.00       0.000      122.00       8.00

============================================================

Reference Node Data

---------------------

===================

Node   Grade Line

No.       m

-------------------

1      146.00

===================

Commercial Diameter Data

--------------------------

====================================

Pipe Dia.   Hazen's    Unit Cost

Int. (mm)   Const    Rs /m   length

------------------------------------

63.0   140.00000       98.00

75.0   140.00000      138.00

90.0   140.00000      189.00

110.0   140.00000      270.00

125.0   140.00000      347.00

140.0   140.00000      432.00

160.0   140.00000      556.00

180.0   140.00000      695.00

200.0   140.00000      789.00

225.0   140.00000     1004.00

250.0   140.00000     1228.00

280.0   140.00000     1532.00

315.0   140.00000     1932.00

355.0   140.00000     2215.00

400.0   140.00000     3147.00

====================================

Branched Water Distribution Network Design OutPut

---------------------------------------------------

Pipe Details

--------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

1    1    2      12.461   140.0 140.00000    0.49     4.90    100.00

2    2   10      10.683   125.0 140.00000    0.39     6.50     60.00

3   10    3       1.778    63.0 140.00000    0.33     6.60     50.00

4   10    4       8.905   110.0 140.00000    6.67     8.55    779.69

Pipe Details  cont`d

---------------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

125.0 140.00000    0.32     4.55     70.31

5    4    5       7.127   110.0 140.00000    1.13     5.65    200.00

6    4    6       1.778    63.0 140.00000    3.08     6.55    470.00

7    2    7       1.778    75.0 140.00000    1.78     2.80    635.00

8    7    8       1.778    63.0 140.00000    0.85     6.56    129.60

75.0 140.00000    1.88     2.80    670.40

============================================================================

Node Details

--------------

=============================================================================

Node    Peak Flow    Elevation    H G L    Cal Pres     Spc Pres   Meet Res

No.       (lps)        (m )        (m )      (m )         (m )    Pres. (Y)

-----------------------------------------------------------------------------

1 S       12.461     126.00     146.00      20.00         8.00

2          0.000     125.90     145.51      19.61         8.00

3 T       -1.778     122.00     144.79      22.79         8.00

4          0.000     126.00     138.13      12.13         8.00

5 T       -7.127     129.00     137.00       8.00         8.00

6 T       -1.778     113.00     135.05      22.05         8.00

7          0.000      99.00     143.73      44.73         8.00

8 T       -1.778     133.00     141.00       8.00         8.00

10          0.000     122.00     145.12      23.12         8.00

=============================================================================

Cost Summary

--------------

=================================================

Diameter    Length        Cost        Cum. Cost

(mm)        (m )      (1000 Rs )    (1000 Rs )

-------------------------------------------------

63.0      649.60         63.66         63.66

75.0     1305.40        180.15        243.81

110.0      979.69        264.52        508.32

125.0      130.31         45.22        553.54

140.0      100.00         43.20        596.74

=================================================

Pipe-wise Cost Summary

------------------------

==========================================================

Pipe   Diameter      Length         Cost       Cum. Cost

No      (mm)        (m )       (1000 Rs )     (1000 Rs )

----------------------------------------------------------

1      140.0       100.00          43.20         43.20

2      125.0        60.00          20.82         64.02

3       63.0        50.00           4.90         68.92

4      110.0       779.69         210.52        279.44

125.0        70.31          24.40        303.83

5      110.0       200.00          54.00        357.83

6       63.0       470.00          46.06        403.89

7       75.0       635.00          87.63        491.52

8       63.0       129.60          12.70        504.22

75.0       670.40          92.52        596.74

ESR 7 – Nandgaon

| S.No. | village | Elevation |  | Population |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | Nandgaon | 120 | 865 | 995 | 1137 |
| 2 | Daunsewadi1 | 116 | 480 | 600 | 800 |
| 3 | Ballvare | 117 | 1168 | 1477 | 1867 |
| 4 | Daunsewadi2 | 110 | 480 | 600 | 800 |
| 5 | Gorechiwadi | 108 | 480 | 600 | 800 |
|  | Total |  | 3473 | 4272 | 5404 |

| Daily Water Demand at 40 lpcd |
| --- |
| S.No. | village | Demand(MLD) | Demand(LPS) |
|  |  | 2011 | 2041 | 2011 | 2041 |
| 1 | Nandgaon | 0.042 | 0.055 | 1.922 | 2.527 |
| 2 | Daunsewadi1 | 0.023 | 0.038 | 1.067 | 1.778 |
| 3 | Ballvare | 0.056 | 0.090 | 2.596 | 4.149 |
| 4 | Daunsewadi2 | 0.023 | 0.038 | 1.067 | 1.778 |
| 5 | Gorechiwadi | 0.023 | 0.038 | 1.067 | 1.778 |
|  | Total | 0.167 | 0.259 | 7.718 | 12.009 |

ESR 7 – Staging Height Optimization

| Total Demand | 259392 |  |  |  |
| --- | --- | --- | --- | --- |
| ESR capacity Required | 97272 |  |  |  |
| ESR capacity Proposed | 98000 |  |  |  |
| Low level Height | 129 |  |  |  |
| ESR elevation | 114 |  |  |  |
| HGL | PIPE cost | ESR cost | Total | height |
| 131 | 862.11 | 757.6028 | 1619.713 | 17 |
| 132 | 822.41 | 778.0785 | 1600.489 | 18 |
| 133 | 790.47 | 798.5543 | 1589.024 | 19 |
| 134 | 758.47 | 819.03 | 1577.5 | 20 |
| 135 | 726.46 | 846.331 | 1572.791 | 21 |
| 136 | 694.44 | 873.632 | 1568.072 | 22 |
| 137 | 668.34 | 900.933 | 1569.273 | 23 |
| 138 | 659.27 | 928.234 | 1587.504 | 24 |
| 139 | 652.04 | 955.535 | 1607.575 | 25 |
| ESR capacity | 487000 |  |  |  |
| Optimum ESR height | 22 |  |  |  |
| ERS cost | 873.63 |  |  |  |
| Pipe cost | 694.44 |  |  |  |
| Total | 1568.07 |  |  |  |
| /person | 290.168764 |  |  |  |

ESR 7 - BRANCH Input and Output

Echoing Input Design Variables

-------------------------------

Title of the Project                   : ESR 7

Name of the User                       :

Number of Pipes                        :  8

Number of Nodes                        :  9

Number of Commercial Diameters         :  15

Peak Design Factor                     :  1

Minimum Headloss in         m/km       :  .1

Maximum Headloss in         m/km       :  25

Minimum Residual Pressure   m          :  8

Type of Formula                        : Hazen's

Branched Water Distribution Network Design OutPut

---------------------------------------------------

Pipe Details

--------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

1    1    2      12.010   140.0 140.00000    0.23     4.60     50.00

2    2    4       1.778    63.0 140.00000    0.98     6.53    150.00

3    2    3       2.527    63.0 140.00000    7.48    12.56    595.65

75.0 140.00000    0.29     5.34     54.35

4    2    5       7.705   125.0 140.00000    0.37     3.52    105.00

5    5    6       4.149    90.0 140.00000   10.17     5.53   1838.63

110.0 140.00000    0.23     2.07    111.37

6    5    7       3.556    63.0 140.00000   12.19    23.62    516.02

75.0 140.00000    0.60    10.17     58.98

7    7    8       1.778    63.0 140.00000    1.38     6.57    210.00

8    7    9       1.778    63.0 140.00000    6.62     6.55   1010.00

============================================================================

Node Details

--------------

=============================================================================

Node    Peak Flow    Elevation    H G L    Cal Pres     Spc Pres   Meet Res

No.       (lps)        (m )        (m )      (m )         (m )    Pres. (Y)

-----------------------------------------------------------------------------

1 S       12.010     114.00     136.00      22.00         8.00

2          0.000     113.90     135.77      21.87         8.00

3 T       -2.527     120.00     128.00       8.00         8.00

4 T       -1.778     116.00     134.79      18.79         8.00

5          0.000     114.00     135.40      21.40         8.00

6 T       -4.149     117.00     125.00       8.00         8.00

7          0.000     106.00     122.62      16.62         8.00

8 T       -1.778     110.00     121.24      11.24         8.00

9 T       -1.778     108.00     116.00       8.00         8.00

=============================================================================

Cost Summary

--------------

=================================================

Diameter    Length        Cost        Cum. Cost

(mm)        (m )      (1000 Rs )    (1000 Rs )

-------------------------------------------------

63.0     2481.66        243.20        243.20

75.0      113.34         15.64        258.84

90.0     1838.63        347.50        606.34

110.0      111.37         30.07        636.41

125.0      105.00         36.44        672.85

140.0       50.00         21.60        694.45

=================================================

Pipe-wise Cost Summary

------------------------

==========================================================

Pipe   Diameter      Length         Cost       Cum. Cost

No      (mm)        (m )       (1000 Rs )     (1000 Rs )

----------------------------------------------------------

1      140.0        50.00          21.60         21.60

2       63.0       150.00          14.70         36.30

3       63.0       595.65          58.37         94.67

75.0        54.35           7.50        102.17

4      125.0       105.00          36.44        138.61

5       90.0      1838.63         347.50        486.11

110.0       111.37          30.07        516.18

6       63.0       516.02          50.57        566.75

75.0        58.98           8.14        574.89

7       63.0       210.00          20.58        595.47

8       63.0      1010.00          98.98        694.45

ESR 8 – Chai

| S.No. | village | Elevation |  | Population |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | Chevne | 87 | 542 | 660 | 795 |
| 2 | Chai | 105 | 902 | 1394 | 2173 |
| 3 | Kotwalwadi | 102 | 480 | 600 | 800 |
| 4 | Zugarachiwadi | 112 | 785 | 911 | 1047 |
|  | Total |  | 2709 | 3565 | 4815 |

| Daily Water Demand at 40 lpcd |
| --- |
| S.No. | village | Demand(MLD) | Demand(LPS) |
|  |  | 2011 | 2041 | 2011 | 2041 |
| 1 | Chevne | 0.026 | 0.038 | 1.204 | 1.767 |
| 2 | Chai | 0.043 | 0.104 | 2.004 | 4.829 |
| 3 | Kotwalwadi | 0.023 | 0.038 | 1.067 | 1.778 |
| 4 | Zugarachiwadi | 0.038 | 0.050 | 1.744 | 2.327 |
| Total |  | 0.130 | 0.231 | 6.020 | 10.700 |

ESR 8 – Staging Height Optimization

| Total Demand | 231120 |  |  |  |
| --- | --- | --- | --- | --- |
| ESR capacity Required | 86670 |  |  |  |
| ESR capacity Proposed | 87000 |  |  |  |
| Low level Height | 121 |  |  |  |
| ESR elevation | 109 |  |  |  |
| HGL | PIPE cost | ESR cost | Total | Height of ESR |
| 128 | 1282.53 | 737.3867 | 2019.917 | 19 |
| 129 | 1223.31 | 756.294 | 1979.604 | 20 |
| 130 | 1179.89 | 781.5038 | 1961.394 | 21 |
| 131 | 1136.48 | 806.7136 | 1943.194 | 22 |
| 132 | 1099.83 | 831.9234 | 1931.753 | 23 |
| 133 | 1068.74 | 857.1332 | 1925.873 | 24 |
| 134 | 1043.79 | 882.343 | 1926.133 | 25 |
| 135 | 1024.47 | 907.5528 | 1932.023 | 26 |
| ESR capacity | 87000 |  |  |  |
| Optimum ESR height | 24 |  |  |  |
| ERS cost | 857.13 |  |  |  |
| Pipe cost | 1068.74 |  |  |  |
| Total | 1926 |  |  |  |

ESR 8 - BRANCH Input and Output

Echoing Input Variables

------------------------

Title of the Project                   : ESR 8(40 LPCD)

Name of the User                       :

Number of Pipes                        :  8

Number of Nodes                        :  9

Number of Commercial Diameters         :  16

Peak Design Factor                     :  1

Minimum Headloss in         m/km       :  .1

Maximum Headloss in         m/km       :  25

Minimum Residual Pressure   m          :  8

Type of Formula                        : Hazen's

Pipe Data

------------

===========================================================

Pipe  From   To     Length    Diameter  Hazen's   Status

No.  Node  Node      m         mm       Const    (E/P)

-----------------------------------------------------------

1     9     5      620.00

2     5     3      180.00

3     5     6     1440.00

4     6     7      250.00

5     7     1      460.00

6     7     8      990.00

7     6     2      150.00

8     8     4       60.00

===========================================================

Node Data

-----------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

1   1.00      -1.778      102.00       8.00

2   1.00      -4.829      105.00       8.00

3   1.00      -1.767       87.00       8.00

4   1.00      -2.327      112.00       8.00

5   1.00       0.000       89.00       8.00

6   1.00       0.000       89.00       8.00

7   1.00       0.000       87.00       8.00

8   1.00       0.000      112.00       8.00

9   1.00       0.000      109.00       8.00

============================================================

Reference Node Data

---------------------

===================

Node   Grade Line

No.       m

-------------------

9      133.00

===================

Commercial Diameter Data

--------------------------

====================================

Pipe Dia.   Hazen's    Unit Cost

Int. (mm)   Const    Rs /m   length

------------------------------------

63.0   140.00000       98.00

75.0   140.00000      138.00

90.0   140.00000      189.00

110.0   140.00000      270.00

125.0   140.00000      347.00

140.0   140.00000      432.00

160.0   140.00000      556.00

180.0   140.00000      695.00

200.0   140.00000      789.00

225.0   140.00000     1004.00

250.0   140.00000     1228.00

280.0   140.00000     1532.00

315.0   140.00000     1932.00

355.0   140.00000     2210.00

400.0   140.00000     3147.00

500.0   140.00000     4000.00

====================================

Branched Water Distribution Network Design OutPut

---------------------------------------------------

Pipe Details

--------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

1    9    5      10.701   125.0 140.00000    3.65     6.44    566.58

140.0 140.00000    0.20     3.74     53.42

2    5    3       1.767    63.0 140.00000    1.17     6.50    180.00

Pipe Details  cont`d

---------------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

3    5    6       8.934   125.0 140.00000    6.65     4.62   1440.00

4    6    7       4.105   110.0 140.00000    0.51     2.04    250.00

5    7    1       1.778    63.0 140.00000    3.01     6.54    460.00

6    7    8       2.327    90.0 140.00000    1.88     1.90    990.00

7    6    2       4.829    75.0 140.00000    2.67    17.80    150.00

8    8    4       2.327    90.0 140.00000    0.11     1.83     60.00

============================================================================

Node Details

--------------

=============================================================================

Node    Peak Flow    Elevation    H G L    Cal Pres     Spc Pres   Meet Res

No.       (lps)        (m )        (m )      (m )         (m )    Pres. (Y)

-----------------------------------------------------------------------------

1 T       -1.778     102.00     118.98      16.98         8.00

2 T       -4.829     105.00     119.83      14.83         8.00

3 T       -1.767      87.00     127.98      40.98         8.00

4 T       -2.327     112.00     120.00       8.00         8.00

5          0.000      89.00     129.15      40.15         8.00

6          0.000      89.00     122.50      33.50         8.00

7          0.000      87.00     121.99      34.99         8.00

8          0.000     112.00     120.11       8.11         8.00

9 S       10.701     109.00     133.00      24.00         8.00

=============================================================================

Cost Summary

--------------

=================================================

Diameter    Length        Cost        Cum. Cost

(mm)        (m )      (1000 Rs )    (1000 Rs )

-------------------------------------------------

63.0      640.00         62.72         62.72

75.0      150.00         20.70         83.42

90.0     1050.00        198.45        281.87

110.0      250.00         67.50        349.37

125.0     2006.58        696.28       1045.65

140.0       53.42         23.08       1068.73

=================================================

Pipe-wise Cost Summary

------------------------

==========================================================

Pipe   Diameter      Length         Cost       Cum. Cost

No      (mm)        (m )       (1000 Rs )     (1000 Rs )

----------------------------------------------------------

1      125.0       566.58         196.60        196.60

140.0        53.42          23.08        219.68

2       63.0       180.00          17.64        237.32

3      125.0      1440.00         499.68        737.00

4      110.0       250.00          67.50        804.50

5       63.0       460.00          45.08        849.58

6       90.0       990.00         187.11       1036.69

7       75.0       150.00          20.70       1057.39

8       90.0        60.00          11.34       1068.73

ESR 9 – Bhopalwadi

| S.No. | Village | Elevation |  | Population |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | Bhopalwadi | 96 | 480 | 600 | 800 |
| 2 | Pendarawadi | 71 | 480 | 600 | 800 |
|  | Total |  | 960 | 1200 | 1600 |

| Daily Water Demand at 40 lpcd |
| --- |
| S.No. | Village | Demand(MLD) | Demand(LPS) |
|  |  | 2011 | 2041 | 2011 | 2041 |
| 1 | Bhopalwadi | 0.023 | 0.038 | 1.067 | 1.778 |
| 2 | Pendarawadi | 0.023 | 0.038 | 1.067 | 1.778 |
|  | Total | 0.046 | 0.077 | 2.133 | 3.556 |

ESR 9 – Staging Height Optimization

|  | 76800 |  |  |  |
| --- | --- | --- | --- | --- |
| ESR capacity Required | 28800 |  |  |  |
| ESR capacity Proposed | 29000 |  |  |  |
| Low level Height | 10 |  |  |  |
| ESR elevation | 95 |  |  |  |
| HGL | PIPE cost | ESR cost | Total | height |
| 105 | 184.67 | 293.9328 | 478.6028 | 10 |
| 106 | 181.3 | 300.0564 | 481.3564 | 11 |
| 107 | 181.3 | 306.18 | 487.48 | 12 |
| 108 | 181.3 | 312.3036 | 493.6036 | 13 |
| 109 | 181.3 | 318.4272 | 499.7272 | 14 |
| 110 | 181.3 | 324.5508 | 505.8508 | 15 |
| 111 | 181.3 | 330.6744 | 511.9744 | 16 |
| 112 | 181.3 | 339.8598 | 521.1598 | 17 |
| 113 | 181.3 | 349.0452 | 530.3452 | 18 |
| 114 | 181.3 | 358.2306 | 539.5306 | 19 |
| ESR capacity | 144000 |  |  |  |
| Optimum ESR height | 10 |  |  |  |
| ERS cost | 293.93 |  |  |  |
| Pipe cost | 184.67 |  |  |  |
| Total | 479 |  |  |  |
| /person | 299.12675 |  |  |  |

ESR 9 - BRANCH Input and Output

Echoing Input Variables

------------------------

Title of the Project                   :ESR 9(40 LPCD)

Name of the User                       :

Number of Pipes                        :  3

Number of Nodes                        :  4

Number of Commercial Diameters         :  16

Peak Design Factor                     :  1

Minimum Headloss in         m/km       :  .1

Maximum Headloss in         m/km       :  25

Minimum Residual Pressure   m          :  8

Type of Formula                        : Hazen's

Pipe Data

------------

===========================================================

Pipe  From   To     Length    Diameter  Hazen's   Status

No.  Node  Node      m         mm       Const    (E/P)

-----------------------------------------------------------

1     1     2       50.00

2     2     3      100.00

3     2     4     1700.00

===========================================================

Node Data

-----------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

1   1.00       0.000       95.00       8.00

2   1.00       0.000       94.90       8.00

3   1.00      -1.778       96.00       8.00

4   1.00      -1.778       71.00       8.00

============================================================

Reference Node Data

---------------------

===================

Node   Grade Line

No.       m

-------------------

1      105.00

===================

Commercial Diameter Data

--------------------------

====================================

Pipe Dia.   Hazen's    Unit Cost

Int. (mm)   Const    Rs /m   length

------------------------------------

63.0   140.00000       98.00

75.0   140.00000      138.00

90.0   140.00000      189.00

110.0   140.00000      270.00

125.0   140.00000      347.00

140.0   140.00000      432.00

160.0   140.00000      556.00

180.0   140.00000      695.00

200.0   140.00000      789.00

225.0   140.00000     1004.00

250.0   140.00000     1228.00

280.0   140.00000     1532.00

315.0   140.00000     1932.00

355.0   140.00000     2210.00

400.0   140.00000     3147.00

500.0   140.00000     4000.00

====================================

Branched Water Distribution Network Design OutPut

---------------------------------------------------

Pipe Details

--------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

1    1    2       3.556    75.0 140.00000    0.23     9.99     23.02

90.0 140.00000    0.11     4.08     26.98

2    2    3       1.778    63.0 140.00000    0.66     6.60    100.00

3    2    4       1.778    63.0 140.00000   11.14     6.55   1700.00

============================================================================

Node Details

--------------

=============================================================================

Node    Peak Flow    Elevation    H G L    Cal Pres     Spc Pres   Meet Res

No.       (lps)        (m )        (m )      (m )         (m )    Pres. (Y)

-----------------------------------------------------------------------------

1 S        3.556      95.00     105.00      10.00         8.00

2          0.000      94.90     104.66       9.76         8.00

3 T       -1.778      96.00     104.00       8.00         8.00

4 T       -1.778      71.00      93.52      22.52         8.00

=============================================================================

Cost Summary

--------------

=================================================

Diameter    Length        Cost        Cum. Cost

(mm)        (m )      (1000 Rs )    (1000 Rs )

-------------------------------------------------

63.0     1800.00        176.40        176.40

75.0       23.02          3.18        179.58

90.0       26.98          5.10        184.68

=================================================

Pipe-wise Cost Summary

------------------------

==========================================================

Pipe   Diameter      Length         Cost       Cum. Cost

No      (mm)        (m )       (1000 Rs )     (1000 Rs )

----------------------------------------------------------

1       75.0        23.02           3.18          3.18

90.0        26.98           5.10          8.28

2       63.0       100.00           9.80         18.08

3       63.0      1700.00         166.60        184.68

ESR 10 – Bondshet

| S.No. | village | Elevation |  | Population |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | Bondshet | 62 | 480 | 600 | 800 |
|  | Total |  | 480 | 600 | 800 |

| Daily Water Demand at 40 lpcd |
| --- |
| S.No. | village | Demand(MLD) | Demand(LPS) |
|  |  | 2011 | 2041 | 2011 | 2041 |
| 1 | Bondshet | 0.023 | 0.038 | 1.067 | 1.778 |
|  | Total | 0.023 | 0.038 | 1.067 | 1.778 |

ESR 10 Design Details

| Total Demand | 38400 |  |  |
| --- | --- | --- | --- |
| ESR capacity Required | 14400 |  |  |
| ESR capacity Proposed | 15000 |  |  |
| Low level Height | 10 |  |  |
| ESR elevation | 62 |  |  |
| HGL | ESR cost | Total | height |
| 72 | 161.86 | 161.86 | 10 |
| ESR capacity | 15000 |  |  |
| Optimum ESR height | 10 |  |  |
| ERS cost | 161.86 |  |  |
| Total | 161.86 |  |  |
| /person | 202.325 |  |  |

ESR 11 – Borgaon

| S.No. | village | Elevation |  | Population |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | Borgaon | 65 | 1095 | 1305 | 1545 |
|  | Total |  | 1095 | 1305 | 1545 |

| Daily Water Demand at 40 lpcd |
| --- |
| S.No. | village | Demand(MLD) | Demand(LPS) |
|  |  | 2011 | 2041 | 2011 | 2041 |
| 1 | Borgaon | 0.053 | 0.074 | 2.433 | 3.433 |
|  | Total | 0.053 | 0.074 | 2.433 | 3.433 |

ESR 11 Design Details

| Total Demand | 74160 |  |  |
| --- | --- | --- | --- |
| ESR capacity Required | 27810 |  |  |
| ESR capacity Proposed | 28000 |  |  |
| Low level Height | 10 |  |  |
| ESR elevation | 65 |  |  |
| HGL | ESR cost | Total | height |
| 75 | 287.91 | 287.91 | 10 |
| ESR capacity | 15000 |  |  |
| Optimum ESR height | 10 |  |  |
| ERS cost | 287.91 |  |  |
| Total | 287.91 |  |  |
| /person | 186.349515 |  |  |

ESR 12 – Aleman

| S.No. | village | Elevation |  | Population |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | Aleman | 162 | 1012 | 1274 | 1587 |
| 2 | Telangwadi | 132 | 480 | 600 | 800 |
| 3 | Borichiwadi | 161 | 480 | 600 | 800 |
| 4 | Bhagyachiwadi | 128 | 480 | 600 | 800 |
|  | Total |  | 2452 | 3074 | 3987 |

| Daily Water Demand at 40 lpcd |
| --- |
| S.No. | village | Demand(MLD) | Demand(LPS) |
|  |  | 2011 | 2041 | 2011 | 2041 |
| 1 | Aleman | 0.049 | 0.076 | 2.250 | 3.526 |
| 2 | Telangwadi | 0.023 | 0.038 | 1.067 | 1.778 |
| 3 | Borichiwadi | 0.023 | 0.038 | 1.067 | 1.778 |
| 4 | Bhagyachiwadi | 0.023 | 0.038 | 1.067 | 1.778 |
|  | Total | 0.118 | 0.191 | 5.450 | 8.859 |

ESR 12 – Staging Height Optimization

| Total Demand | 191355 |  |  |  |
| --- | --- | --- | --- | --- |
| ESR capacity Required | 71758 |  |  |  |
| ESR capacity Proposed | 72000 |  |  |  |
| Low level Height | 173 |  |  |  |
| ESR elevation | 165 |  |  |  |
| HGL | PIPE cost | ESR cost | Total | height |
| 173 | 820.62 | 511.8834 | 1332.503 | 8 |
| 174 | 787.23 | 523.0113 | 1310.241 | 9 |
| 175 | 756.03 | 534.1392 | 1290.169 | 10 |
| 176 | 740.12 | 545.2671 | 1285.387 | 11 |
| 177 | 731.55 | 556.395 | 1287.945 | 12 |
| 178 | 722.98 | 567.5229 | 1290.503 | 13 |
| 179 | 714.39 | 578.6508 | 1293.041 | 14 |
| 180 | 705.82 | 589.7787 | 1295.599 | 15 |
| 181 | 697.25 | 600.9066 | 1298.157 | 16 |
| 182 | 688.66 | 617.5985 | 1306.258 | 17 |
| Optimum ESR height | 11 |  |  |  |
| ERS cost | 545.27 |  |  |  |
| Pipe cost | 740.12 |  |  |  |
| Total | 1285.39 |  |  |  |
| /person | 322 |  |  |  |

ESR 12 - BRANCH Input and Output

Echoing Input Variables

------------------------

Title of the Project                   :ESR 12(40 LPCD)

Name of the User                       :

Number of Pipes                        :  7

Number of Nodes                        :  8

Number of Commercial Diameters         :  16

Peak Design Factor                     :  1

Minimum Headloss in         m/km       :  .1

Maximum Headloss in         m/km       :  25

Minimum Residual Pressure   m          :  8

Type of Formula                        : Hazen's

Pipe Data

------------

===========================================================

Pipe  From   To     Length    Diameter  Hazen's   Status

No.  Node  Node      m         mm       Const    (E/P)

-----------------------------------------------------------

1     1     2       50.00

2     2     3      150.00

3     2     4     2000.00

4     2     5      765.00

5     5     6      565.00

6     6     7      150.00

7     6     8     2555.00

===========================================================

Node Data

-----------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

1   1.00       0.000      165.00       8.00

2   1.00       0.000      164.90       8.00

3   1.00      -3.526      162.00       8.00

4   1.00      -1.778      132.00       8.00

5   1.00       0.000      160.00       8.00

6   1.00       0.000      161.00       8.00

7   1.00      -1.778      161.00       8.00

8   1.00      -1.778      128.00       8.00

============================================================

Reference Node Data

---------------------

===================

Node   Grade Line

No.       m

-------------------

1      176.00

===================

Commercial Diameter Data

--------------------------

====================================

Pipe Dia.   Hazen's    Unit Cost

Int. (mm)   Const    Rs /m   length

------------------------------------

63.0   140.00000       98.00

75.0   140.00000      138.00

90.0   140.00000      189.00

110.0   140.00000      270.00

125.0   140.00000      347.00

140.0   140.00000      432.00

160.0   140.00000      556.00

180.0   140.00000      695.00

200.0   140.00000      789.00

225.0   140.00000     1004.00

250.0   140.00000     1228.00

280.0   140.00000     1532.00

315.0   140.00000     1932.00

355.0   140.00000     2210.00

400.0   140.00000     3147.00

500.0   140.00000     4000.00

====================================

Branched Water Distribution Network Design OutPut

---------------------------------------------------

Pipe Details

--------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

1    1    2       8.860   110.0 140.00000    0.42     8.40     50.00

2    2    3       3.526    63.0 140.00000    3.49    23.27    150.00

3    2    4       1.778    63.0 140.00000   13.10     6.55   2000.00

Pipe Details  cont`d

---------------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

4    2    5       3.556    75.0 140.00000    0.11    10.34     10.64

90.0 140.00000    3.14     4.16    754.36

5    5    6       3.556    90.0 140.00000    2.35     4.16    565.00

6    6    7       1.778    63.0 140.00000    0.98     6.53    150.00

7    6    8       1.778    63.0 140.00000   16.74     6.55   2555.00

============================================================================

Node Details

--------------

=============================================================================

Node    Peak Flow    Elevation    H G L    Cal Pres     Spc Pres   Meet Res

No.       (lps)        (m )        (m )      (m )         (m )    Pres. (Y)

-----------------------------------------------------------------------------

1 S        8.860     165.00     176.00      11.00         8.00

2          0.000     164.90     175.58      10.68         8.00

3 T       -3.526     162.00     172.09      10.09         8.00

4 T       -1.778     132.00     162.47      30.47         8.00

5          0.000     160.00     172.33      12.33         8.00

6          0.000     161.00     169.98       8.98         8.00

7 T       -1.778     161.00     169.00       8.00         8.00

8 T       -1.778     128.00     153.24      25.24         8.00

=============================================================================

Cost Summary

--------------

=================================================

Diameter    Length        Cost        Cum. Cost

(mm)        (m )      (1000 Rs )    (1000 Rs )

-------------------------------------------------

63.0     4855.00        475.79        475.79

75.0       10.64          1.47        477.26

90.0     1319.36        249.36        726.62

110.0       50.00         13.50        740.12

=================================================

Pipe-wise Cost Summary

------------------------

==========================================================

Pipe   Diameter      Length         Cost       Cum. Cost

No      (mm)        (m )       (1000 Rs )     (1000 Rs )

----------------------------------------------------------

1      110.0        50.00          13.50         13.50

2       63.0       150.00          14.70         28.20

3       63.0      2000.00         196.00        224.20

4       75.0        10.64           1.47        225.67

90.0       754.36         142.57        368.24

5       90.0       565.00         106.79        475.03

6       63.0       150.00          14.70        489.73

7       63.0      2555.00         250.39        740.12

ESR 13 – Murchulwadi

| S.No. | village | Elevation |  | Population |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | Murchulwadi | 153 | 480 | 600 | 800 |
| 2 | Bhikarwadi | 136 | 480 | 600 | 800 |
| 3 | Narthewadi | 119 | 480 | 600 | 800 |
|  | Total |  | 1440 | 1800 | 2400 |

| Daily Water Demand at 40 lpcd |
| --- |
| S.No. |  | Demand(MLD) |  | Demand(LPS) |  |
|  | village | 2011 | 2041 | 2011 | 2041 |
| 1 | Murchulwadi | 0.115 | 0.192 | 5.333 | 8.889 |
| 2 | Bhikarwadi | 0.115 | 0.192 | 5.333 | 8.889 |
| 3 | Narthewadi | 0.115 | 0.192 | 5.333 | 8.889 |
|  | Total | 0.346 | 0.576 | 16.000 | 26.667 |

ESR 13 – Staging Height Optimization

| Total Demand | 115200 |  |  |  |
| --- | --- | --- | --- | --- |
| ESR capacity Required | 43200 |  |  |  |
| ESR capacity Proposed | 44000 |  |  |  |
| Low level Height | 162 |  |  |  |
| ESR elevation | 153 |  |  |  |
| HGL | PIPE cost | ESR cost | Total | height |
| 162 | 334.411 | 376.3572 | 710.7682 | 9 |
| 163 | 321.46 | 384.3648 | 705.8248 | 10 |
| 164 | 317.4 | 392.3724 | 709.7724 | 11 |
| 165 | 314.31 | 400.38 | 714.69 | 12 |
| 166 | 311.35 | 408.3876 | 719.7376 | 13 |
| 167 | 308.39 | 416.3952 | 724.7852 | 14 |
| 168 | 307.8 | 424.4028 | 732.2028 | 15 |
| 169 | 307.8 | 432.4104 | 740.2104 | 16 |
| 170 | 307.8 | 444.4218 | 752.2218 | 17 |
| Optimum ESR height | 10 |  |  |  |
| ERS cost | 384.36 |  |  |  |
| Pipe cost | 321.46 |  |  |  |
| Total | 705.82 |  |  |  |
| /person | 294 |  |  |  |

ESR 13 - BRANCH Input and Output

Echoing Input Variables

------------------------

Title of the Project                   :ESR 13(40 LPCD)

Name of the User                       :

Number of Pipes                        :  6

Number of Nodes                        :  7

Number of Commercial Diameters         :  16

Peak Design Factor                     :  1

Minimum Headloss in         m/km       :  .1

Maximum Headloss in         m/km       :  25

Minimum Residual Pressure   m          :  8

Type of Formula                        : Hazen's

Pipe Data

------------

===========================================================

Pipe  From   To     Length    Diameter  Hazen's   Status

No.  Node  Node      m         mm       Const    (E/P)

-----------------------------------------------------------

1     1     2      100.00

2     2     3      150.00

3     2     4      850.00

4     4     5      150.00

5     4     6     1700.00

6     6     7      150.00

===========================================================

Node Data

-----------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

1   1.00       0.000      153.00       8.00

2   1.00       0.000      152.90       8.00

3   1.00      -1.778      153.00       8.00

4   1.00       0.000      134.00       8.00

5   1.00      -1.778      136.00       8.00

6   1.00       0.000      119.00       8.00

7   1.00      -1.778      119.00       8.00

============================================================

Reference Node Data

---------------------

===================

Node   Grade Line

No.       m

-------------------

1      163.00

===================

Commercial Diameter Data

--------------------------

====================================

Pipe Dia.   Hazen's    Unit Cost

Int. (mm)   Const    Rs /m   length

------------------------------------

63.0   140.00000       98.00

75.0   140.00000      138.00

90.0   140.00000      189.00

110.0   140.00000      270.00

125.0   140.00000      347.00

140.0   140.00000      432.00

160.0   140.00000      556.00

180.0   140.00000      695.00

200.0   140.00000      789.00

225.0   140.00000     1004.00

250.0   140.00000     1228.00

280.0   140.00000     1532.00

315.0   140.00000     1932.00

355.0   140.00000     2210.00

400.0   140.00000     3147.00

500.0   140.00000     4000.00

====================================

Branched Water Distribution Network Design OutPut

---------------------------------------------------

Pipe Details

--------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

1    1    2       5.334    75.0 140.00000    0.23    21.16     10.87

90.0 140.00000    0.78     8.75     89.13

2    2    3       1.778    63.0 140.00000    0.98     6.53    150.00

3    2    4       3.556    63.0 140.00000   14.70    23.62    622.35

75.0 140.00000    2.30    10.10    227.65

4    4    5       1.778    63.0 140.00000    0.98     6.53    150.00

5    4    6       1.778    63.0 140.00000   11.14     6.55   1700.00

6    6    7       1.778    63.0 140.00000    0.98     6.53    150.00

Node Details

--------------

=============================================================================

Node    Peak Flow    Elevation    H G L    Cal Pres     Spc Pres   Meet Res

No.       (lps)        (m )        (m )      (m )         (m )    Pres. (Y)

-----------------------------------------------------------------------------

1 S        5.334     153.00     163.00      10.00         8.00

2          0.000     152.90     161.98       9.08         8.00

3 T       -1.778     153.00     161.00       8.00         8.00

4          0.000     134.00     144.98      10.98         8.00

5 T       -1.778     136.00     144.00       8.00         8.00

6          0.000     119.00     133.84      14.84         8.00

7 T       -1.778     119.00     132.86      13.86         8.00

=============================================================================

Cost Summary

--------------

=================================================

Diameter    Length        Cost        Cum. Cost

(mm)        (m )      (1000 Rs )    (1000 Rs )

-------------------------------------------------

63.0     2772.35        271.69        271.69

75.0      238.52         32.92        304.61

90.0       89.13         16.85        321.45

=================================================

Pipe-wise Cost Summary

------------------------

==========================================================

Pipe   Diameter      Length         Cost       Cum. Cost

No      (mm)        (m )       (1000 Rs )     (1000 Rs )

----------------------------------------------------------

1       75.0        10.87           1.50          1.50

90.0        89.13          16.85         18.35

2       63.0       150.00          14.70         33.05

3       63.0       622.35          60.99         94.04

75.0       227.65          31.42        125.45

4       63.0       150.00          14.70        140.15

5       63.0      1700.00         166.60        306.75

6       63.0       150.00          14.70        321.45

ESR 14 – Kalamb

| S.No. | village | Elevation |  | Population |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | Kalamb | 50 | 4691 | 5814 | 7140 |
|  | Total |  | 4691 | 5814 | 7140 |

| Daily Water Demand at 40 lpcd |
| --- |
| S.No. | village | Demand(MLD) | Demand(LPS) |
|  |  | 2011 | 2041 | 2011 | 2041 |
| 1 | Kalamb | 0.225 | 0.343 | 10.425 | 15.867 |
|  | Total | 0.225 | 0.343 | 10.425 | 15.867 |

ESR 14 Design Details

| Total Demand | 342721 |  |  |
| --- | --- | --- | --- |
| ESR capacity Required | 128520 |  |  |
| ESR capacity Proposed | 130000 |  |  |
| Low level Height | 14 |  |  |
| ESR elevation | 43 |  |  |
| HGL | ESR cost | Total | height |
| 57 | 837.5 | 837.5 | 14 |
| ESR capacity | 130000 |  |  |
| Optimum ESR height | 12 |  |  |
| ERS cost | 837.50 |  |  |
| Total | 837.50 |  |  |
| /person | 117.30 |  |  |

ESR 15 – Salokh

| S.No. | Village | Elevation |  | Population |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | Salokh | 47 | 1788 | 2165 | 2601 |
|  | Total |  | 1788 | 2165 | 2601 |

| Daily Water Demand at 40 lpcd |
| --- |
| S.No. | village | Demand(MLD) | Demand(LPS) |
|  |  | 2011 | 2041 | 2011 | 2041 |
| 1 | Salokh | 0.086 | 0.125 | 3.973 | 5.780 |
|  | Total | 0.086 | 0.125 | 3.973 | 5.780 |

ESR 15 Design Details

| Total Demand | 124848 |  |  |
| --- | --- | --- | --- |
| ESR capacity Required | 46818 |  |  |
| ESR capacity Proposed | 47000 |  |  |
| Low level Height | 10 |  |  |
| ESR elevation | 47 |  |  |
| HGL | ESR cost | Total | height |
| 57 | 419.22 | 419.22 | 10 |
| ESR capacity | 47000 |  |  |
| Optimum ESR height | 10 |  |  |
| ERS cost | 419.22 |  |  |
| Total | 419.22 |  |  |
| /person | 161.18 |  |  |

ESR 16 – Male

| S.No. | Village | Elevation |  | Population |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | Poshir | 45 | 2624 | 2962 | 3332 |
| 2 | Charnpada | 40 | 480 | 600 | 800 |
| 3 | Ase | 43 | 215 | 303 | 427 |
| 4 | Ardhe | 59 | 854 | 1062 | 1308 |
| 5 | Male | 53 | 1573 | 1934 | 2370 |
| 6 | Palanpada | 48 | 480 | 600 | 800 |
|  | Total |  | 6226 | 7461 | 9038 |

| Daily Water Demand at 40 lpcd |
| --- |
| S.No. | Village | Demand(MLD) | Demand(LPS) |
|  |  | 2011 | 2041 | 2011 | 2041 |
| 1 | Poshir | 0.126 | 0.160 | 5.830 | 7.405 |
| 2 | Charnpada | 0.023 | 0.038 | 1.067 | 1.778 |
| 3 | Ase | 0.010 | 0.021 | 0.478 | 0.950 |
| 4 | Ardhe | 0.041 | 0.063 | 1.898 | 2.906 |
| 5 | Male | 0.076 | 0.114 | 3.497 | 5.267 |
| 6 | Palanpada | 0.023 | 0.038 | 1.067 | 1.778 |
|  | Total | 0.299 | 0.434 | 13.836 | 20.084 |

ESR 16 – Staging Height Optimization

| Total Demand | 433816 |  |  |  |
| --- | --- | --- | --- | --- |
| ESR capacity Required | 162681 |  |  |  |
| ESR capacity Proposed | 165000 |  |  |  |
| Low level Height | 68 |  |  |  |
| ESR elevation | 56 |  |  |  |
| HGL | PIPE cost | ESR cost | Total | height |
| 72 | 1144.29 | 976.05 | 2120.34 | 16 |
| 73 | 1104.99 | 1003.163 | 2108.153 | 17 |
| 74 | 1078.12 | 1030.275 | 2108.395 | 18 |
| 75 | 1054.74 | 1057.388 | 2112.128 | 19 |
| 76 | 1034.26 | 1084.5 | 2118.76 | 20 |
| 77 | 1013.74 | 1120.65 | 2134.39 | 21 |
| 78 | 997.01 | 1156.8 | 2153.81 | 22 |
| ESR capacity | 165000 |  |  |  |
| Optimum ESR height | 17 |  |  |  |
| ERS cost | 1003 |  |  |  |
| Pipe cost | 1104.99 |  |  |  |
| Total | 2108 |  |  |  |
| /person | 233.26 |  |  |  |

ESR 16 - BRANCH Input and Output

Echoing Input Variables

------------------------

Title of the Project                   :ESR 16(40 LPCD)

Name of the User                       :

Number of Pipes                        :  12

Number of Nodes                        :  13

Number of Commercial Diameters         :  16

Peak Design Factor                     :  1

Minimum Headloss in         m/km       :  .1

Maximum Headloss in         m/km       :  25

Minimum Residual Pressure   m          :  8

Type of Formula                        : Hazen's

Pipe Data

------------

===========================================================

Pipe  From   To     Length    Diameter  Hazen's   Status

No.  Node  Node      m         mm       Const    (E/P)

-----------------------------------------------------------

1    11    12       50.00

2    12     7      460.00

3    12     6      240.00

4     7     8      940.00

5     6     9     1450.00

6     9    10      400.00

7    10     1      360.00

8     9     2       70.00

9     6     5       70.00

10     8     4      130.00

11     7     3       20.00

12     6    13      760.00

===========================================================

Node Data

-----------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

1   1.00      -7.405       45.00       8.00

2   1.00      -1.778       40.00       8.00

3   1.00      -0.950       43.00       8.00

4   1.00      -2.906       59.00       8.00

5   1.00      -5.267       53.00       8.00

Node Data  cont`d

------------------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

6   1.00       0.000       45.00       8.00

7   1.00       0.000       41.00       8.00

8   1.00       0.000       43.00       8.00

9   1.00       0.000       27.00       8.00

10   1.00       0.000       35.00       8.00

11   1.00       0.000       56.00       8.00

12   1.00       0.000       55.90       8.00

13   1.00      -1.778       48.00       8.00

============================================================

Reference Node Data

---------------------

===================

Node   Grade Line

No.       m

-------------------

11       73.00

===================

Commercial Diameter Data

--------------------------

====================================

Pipe Dia.   Hazen's    Unit Cost

Int. (mm)   Const    Rs /m   length

------------------------------------

63.0   140.00000       98.00

75.0   140.00000      138.00

90.0   140.00000      189.00

110.0   140.00000      270.00

125.0   140.00000      347.00

140.0   140.00000      432.00

160.0   140.00000      556.00

180.0   140.00000      695.00

200.0   140.00000      789.00

225.0   140.00000     1004.00

250.0   140.00000     1228.00

280.0   140.00000     1532.00

315.0   140.00000     1932.00

355.0   140.00000     2210.00

400.0   140.00000     3147.00

500.0   140.00000     4000.00

====================================

Branched Water Distribution Network Design OutPut

---------------------------------------------------

Pipe Details

--------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

1   11   12      20.084   160.0 140.00000    0.31     6.20     50.00

2   12    7       3.856    90.0 140.00000    2.22     4.83    460.00

3   12    6      16.228   125.0 140.00000    0.05    14.58      3.43

140.0 140.00000    1.90     8.03    236.57

4    7    8       2.906    90.0 140.00000    2.69     2.86    940.00

5    6    9       9.183   110.0 140.00000   13.12     9.05   1450.00

6    9   10       7.405   110.0 140.00000    2.43     6.08    400.00

7   10    1       7.405   110.0 140.00000    2.19     6.08    360.00

8    9    2       1.778    63.0 140.00000    0.46     6.57     70.00

9    6    5       5.267    75.0 140.00000    1.46    20.86     70.00

10    8    4       2.906    75.0 140.00000    0.69     6.98     98.92

90.0 140.00000    0.09     2.90     31.08

11    7    3       0.950    63.0 140.00000    0.04     2.00     20.00

12    6   13       1.778    63.0 140.00000    4.98     6.55    760.00

============================================================================

Node Details

--------------

=============================================================================

Node    Peak Flow    Elevation    H G L    Cal Pres     Spc Pres   Meet Res

No.       (lps)        (m )        (m )      (m )         (m )    Pres. (Y)

-----------------------------------------------------------------------------

1 T       -7.405      45.00      53.00       8.00         8.00

2 T       -1.778      40.00      57.16      17.16         8.00

3 T       -0.950      43.00      70.43      27.43         8.00

4 T       -2.906      59.00      67.00       8.00         8.00

5 T       -5.267      53.00      69.28      16.28         8.00

6          0.000      45.00      70.74      25.74         8.00

7          0.000      41.00      70.47      29.47         8.00

8          0.000      43.00      67.78      24.78         8.00

9          0.000      27.00      57.62      30.62         8.00

10          0.000      35.00      55.19      20.19         8.00

11 S       20.084      56.00      73.00      17.00         8.00

12          0.000      55.90      72.69      16.79         8.00

13 T       -1.778      48.00      65.77      17.77         8.00

=============================================================================

Cost Summary

--------------

=================================================

Diameter    Length        Cost        Cum. Cost

(mm)        (m )      (1000 Rs )    (1000 Rs )

-------------------------------------------------

63.0      850.00         83.30         83.30

75.0      168.92         23.31        106.61

90.0     1431.08        270.47        377.08

110.0     2210.00        596.70        973.78

125.0        3.43          1.19        974.97

140.0      236.57        102.20       1077.17

160.0       50.00         27.80       1104.97

=================================================

Pipe-wise Cost Summary

------------------------

==========================================================

Pipe   Diameter      Length         Cost       Cum. Cost

No      (mm)        (m )       (1000 Rs )     (1000 Rs )

----------------------------------------------------------

1      160.0        50.00          27.80         27.80

2       90.0       460.00          86.94        114.74

3      125.0         3.43           1.19        115.93

140.0       236.57         102.20        218.13

4       90.0       940.00         177.66        395.79

5      110.0      1450.00         391.50        787.29

6      110.0       400.00         108.00        895.29

7      110.0       360.00          97.20        992.49

8       63.0        70.00           6.86        999.35

9       75.0        70.00           9.66       1009.01

10       75.0        98.92          13.65       1022.66

90.0        31.08           5.87       1028.53

11       63.0        20.00           1.96       1030.49

12       63.0       760.00          74.48       1104.97

ESR 17 – Vara

| S.No. | village | Elevation |  | Population |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | ware | 65 | 1755 | 2009 | 2286 |
| 2 | khairpada | 54 | 480 | 600 | 800 |
| 3 | mankivili | 56 | 480 | 600 | 800 |
| 4 | poi | 46 | 436 | 551 | 695 |
|  | Total |  | 3151 | 3760 | 4581 |

| Daily Water Demand at 40 lpcd |
| --- |
| S.No. | village | Demand(MLD) | Demand(LPS) |
|  |  | 2011 | 2041 | 2011 | 2041 |
| 1 | ware | 0.084 | 0.110 | 3.899 | 5.081 |
| 2 | khairpada | 0.023 | 0.038 | 1.067 | 1.778 |
| 3 | mankivili | 0.023 | 0.038 | 1.067 | 1.778 |
| 4 | poi | 0.021 | 0.033 | 0.970 | 1.544 |
| Total |  | 0.151 | 0.220 | 7.002 | 10.180 |

ESR 17 – Staging Height Optimization

| Total Demand | 219895 |  |  |  |
| --- | --- | --- | --- | --- |
| ESR capacity Required | 82461 |  |  |  |
| ESR capacity Proposed | 83000 |  |  |  |
| Low level Height | 74 |  |  |  |
| ESR elevation | 58 |  |  |  |
| HGL | PIPE cost | ESR cost | Total | height |
| 74 | 585.83 | 711.315 | 1297.145 | 16 |
| 75 | 559.02 | 731.0738 | 1290.094 | 17 |
| 76 | 543.48 | 750.8325 | 1294.313 | 18 |
| 77 | 534.39 | 770.5913 | 1304.981 | 19 |
| 78 | 526.23 | 790.35 | 1316.58 | 20 |
| 79 | 521.83 | 816.695 | 1338.525 | 21 |
| 80 | 517.42 | 843.04 | 1360.46 | 22 |
| ESR capacity | 83000 |  |  |  |
| Optimum ESR height | 17 |  |  |  |
| ERS cost | 731 |  |  |  |
| Pipe cost | 559.02 |  |  |  |
| Total | 1290 |  |  |  |
| /person | 281.61 |  |  |  |

ESR 17 - BRANCH Input and Output

Echoing Input Variables

------------------------

Title of the Project                   :ESR 17(40 LPCD)

Name of the User                       :

Number of Pipes                        :  7

Number of Nodes                        :  8

Number of Commercial Diameters         :  16

Peak Design Factor                     :  1

Minimum Headloss in         m/km       :  .1

Maximum Headloss in         m/km       :  25

Minimum Residual Pressure   m          :  8

Type of Formula                        : Hazen's

Pipe Data

------------

===========================================================

Pipe  From   To     Length    Diameter  Hazen's   Status

No.  Node  Node      m         mm       Const    (E/P)

-----------------------------------------------------------

1     1     2       50.00

2     2     3      220.00

3     2     4      710.00

4     4     5      760.00

5     4     6       75.00

6     6     7      775.00

7     6     8     2000.00

===========================================================

Node Data

-----------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

1   1.00       0.000       58.00       8.00

2   1.00       0.000       57.90       8.00

3   1.00      -5.081       65.00       8.00

4   1.00       0.000       50.00       8.00

5   1.00      -1.778       54.00       8.00

6   1.00       0.000       51.00       8.00

7   1.00      -1.778       56.00       8.00

8   1.00      -1.544       46.00       8.00

============================================================

Reference Node Data

---------------------

===================

Node   Grade Line

No.       m

-------------------

1       75.00

===================

Commercial Diameter Data

--------------------------

====================================

Pipe Dia.   Hazen's    Unit Cost

Int. (mm)   Const    Rs /m   length

------------------------------------

63.0   140.00000       98.00

75.0   140.00000      138.00

90.0   140.00000      189.00

110.0   140.00000      270.00

125.0   140.00000      347.00

140.0   140.00000      432.00

160.0   140.00000      556.00

180.0   140.00000      695.00

200.0   140.00000      789.00

225.0   140.00000     1004.00

250.0   140.00000     1228.00

280.0   140.00000     1532.00

315.0   140.00000     1932.00

355.0   140.00000     2210.00

400.0   140.00000     3147.00

500.0   140.00000     4000.00

====================================

Branched Water Distribution Network Design OutPut

---------------------------------------------------

Pipe Details

--------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

1    1    2      10.181   125.0 140.00000    0.29     5.80     50.00

2    2    3       5.081    90.0 140.00000    1.67     8.06    207.20

110.0 140.00000    0.04     3.13     12.80

Pipe Details  cont`d

---------------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

3    2    4       5.100    90.0 140.00000    5.75     8.10    710.00

4    4    5       1.778    63.0 140.00000    4.98     6.55    760.00

5    4    6       3.322    90.0 140.00000    0.27     3.60     75.00

6    6    7       1.778    63.0 140.00000    4.38     6.55    668.43

75.0 140.00000    0.30     2.82    106.57

7    6    8       1.544    63.0 140.00000   10.09     5.05   2000.00

============================================================================

Node Details

--------------

=============================================================================

Node    Peak Flow    Elevation    H G L    Cal Pres     Spc Pres   Meet Res

No.       (lps)        (m )        (m )      (m )         (m )    Pres. (Y)

-----------------------------------------------------------------------------

1 S       10.181      58.00      75.00      17.00         8.00

2          0.000      57.90      74.71      16.81         8.00

3 T       -5.081      65.00      73.00       8.00         8.00

4          0.000      50.00      68.95      18.95         8.00

5 T       -1.778      54.00      63.97       9.97         8.00

6          0.000      51.00      68.68      17.68         8.00

7 T       -1.778      56.00      64.00       8.00         8.00

8 T       -1.544      46.00      58.59      12.59         8.00

=============================================================================

Cost Summary

--------------

=================================================

Diameter    Length        Cost        Cum. Cost

(mm)        (m )      (1000 Rs )    (1000 Rs )

-------------------------------------------------

63.0     3428.43        335.99        335.99

75.0      106.57         14.71        350.69

90.0      992.20        187.53        538.22

110.0       12.80          3.46        541.67

125.0       50.00         17.35        559.02

=================================================

Pipe-wise Cost Summary

------------------------

==========================================================

Pipe   Diameter      Length         Cost       Cum. Cost

No      (mm)        (m )       (1000 Rs )     (1000 Rs )

----------------------------------------------------------

1      125.0        50.00          17.35         17.35

2       90.0       207.20          39.16         56.51

110.0        12.80           3.46         59.97

3       90.0       710.00         134.19        194.16

4       63.0       760.00          74.48        268.64

5       90.0        75.00          14.18        282.81

6       63.0       668.43          65.51        348.32

75.0       106.57          14.71        363.02

7       63.0      2000.00         196.00        559.02

ESR 18 – Chinchpada

| S.No. | village | Elevation |  | Population |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | Chinchpada | 128 | 480 | 600 | 800 |
| 2 | Devpada | 87 | 480 | 600 | 800 |
| 3 | Giripada | 118 | 480 | 600 | 800 |
| 4 | Umberwadi2 | 105 | 480 | 600 | 800 |
| 5 | Umberwadi1 | 103 | 480 | 600 | 800 |
| 6 | Banjarpada | 61 | 480 | 600 | 800 |
| 7 | Talwade Budruk | 57 | 480 | 600 | 800 |
|  | Total |  | 3360 | 4200 | 5600 |

| Daily Water Demand at 40 lpcd |
| --- |
| S.No. | village | Demand(MLD) | Demand(LPS) |
|  |  | 2011 | 2041 | 2011 | 2041 |
| 1 | Chinchpada |  |  |  |  |
| 2 | Devpada |  |  |  |  |
| 3 | Giripada |  |  |  |  |
| 4 | Umberwadi2 |  |  |  |  |
| 5 | Umberwadi1 |  |  |  |  |
| 6 | Banjarpada |  |  |  |  |
| 7 | Talwade Budruk |  |  |  |  |
|  | Total |  |  |  |  |

ESR 18 – Staging Height Optimization

| Total Demand | 268800 |  |  |  |
| --- | --- | --- | --- | --- |
| ESR capacity Required | 100800 |  |  |  |
| ESR capacity Proposed | 101000 |  |  |  |
| Low level Height | 137 |  |  |  |
| ESR elevation | 128 |  |  |  |
| HGL | PIPE cost | ESR cost | Total | height |
| 139 | 1228.46 | 682.0359 | 1910.496 | 11 |
| 140 | 1208.97 | 695.955 | 1904.925 | 12 |
| 141 | 1189.48 | 709.8741 | 1899.354 | 13 |
| 142 | 1174.5 | 723.7932 | 1898.293 | 14 |
| 143 | 1160.52 | 737.7123 | 1898.232 | 15 |
| 144 | 1146.61 | 751.6314 | 1898.241 | 16 |
| 145 | 1132.7 | 772.5101 | 1905.21 | 17 |
| 146 | 1118.79 | 793.3887 | 1912.179 | 18 |
| ESR capacity | 101000 |  |  |  |
| Optimum ESR height | 15 |  |  |  |
| ERS cost | 738 |  |  |  |
| Pipe cost | 1160.52 |  |  |  |
| Total | 1898 |  |  |  |
| /person | 338.97 |  |  |  |

ESR 18 - BRANCH Input and Output

Echoing Input Variables

------------------------

Title of the Project                   :ESR 18(40 LPCD)

Name of the User                       :

Number of Pipes                        :  13

Number of Nodes                        :  14

Number of Commercial Diameters         :  16

Peak Design Factor                     :  1

Minimum Headloss in         m/km       :  .1

Maximum Headloss in         m/km       :  25

Minimum Residual Pressure   m          :  8

Type of Formula                        : Hazen's

Pipe Data

------------

===========================================================

Pipe  From   To     Length    Diameter  Hazen's   Status

No.  Node  Node      m         mm       Const    (E/P)

-----------------------------------------------------------

1    14     8       50.00

2     8     1      140.00

3     8     9     1300.00

4     9     2      100.00

5     9    10      650.00

6    10     3      270.00

7    10    11      500.00

8    11     4      520.00

9    11    12      420.00

10    12    13     1180.00

11    13     6      100.00

12    12     5      590.00

13    13     7      800.00

===========================================================

Node Data

-----------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

1   1.00      -1.778      128.00       8.00

2   1.00      -1.778       87.00       8.00

3   1.00      -1.778      118.00       8.00

4   1.00      -1.778      105.00       8.00

Node Data  cont`d

------------------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

5   1.00      -1.778      103.00       8.00

6   1.00      -1.778       61.00       8.00

7   1.00      -1.778       57.00       8.00

8   1.00       0.000      127.80       8.00

9   1.00       0.000       74.00       8.00

10   1.00       0.000      109.00       8.00

11   1.00       0.000      103.00       8.00

12   1.00       0.000      108.00       8.00

13   1.00       0.000       61.00       8.00

14   1.00       0.000      128.00       8.00

============================================================

Reference Node Data

---------------------

===================

Node   Grade Line

No.       m

-------------------

14      143.00

===================

Commercial Diameter Data

--------------------------

====================================

Pipe Dia.   Hazen's    Unit Cost

Int. (mm)   Const    Rs /m   length

------------------------------------

63.0   140.00000       98.00

75.0   140.00000      138.00

90.0   140.00000      189.00

110.0   140.00000      270.00

125.0   140.00000      347.00

140.0   140.00000      432.00

160.0   140.00000      556.00

180.0   140.00000      695.00

200.0   140.00000      789.00

225.0   140.00000     1004.00

250.0   140.00000     1228.00

280.0   140.00000     1532.00

315.0   140.00000     1932.00

355.0   140.00000     2210.00

Commercial Diameter Data  cont`d

---------------------------------

====================================

Pipe Dia.   Hazen's    Unit Cost

Int. (mm)   Const    Rs /m   length

------------------------------------

400.0   140.00000     3147.00

500.0   140.00000     4000.00

====================================

Branched Water Distribution Network Design OutPut

---------------------------------------------------

Pipe Details

--------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

1   14    8      12.446   125.0 140.00000    0.43     8.60     50.00

2    8    1       1.778    63.0 140.00000    0.92     6.57    140.00

3    8    9      10.668   110.0 140.00000    2.01    11.93    168.42

125.0 140.00000    7.25     6.41   1131.58

4    9    2       1.778    63.0 140.00000    0.66     6.60    100.00

5    9   10       8.890   110.0 140.00000    5.54     8.52    650.00

6   10    3       1.778    63.0 140.00000    1.77     6.56    270.00

7   10   11       7.112    90.0 140.00000    7.50    15.00    500.00

8   11    4       1.778    63.0 140.00000    3.41     6.56    520.00

9   11   12       5.334    75.0 140.00000    2.91    21.42    135.88

90.0 140.00000    2.50     8.80    284.12

10   12   13       3.556    63.0 140.00000   27.87    23.62   1180.00

11   13    6       1.778    63.0 140.00000    0.66     6.60    100.00

12   12    5       1.778    63.0 140.00000    3.87     6.56    590.00

13   13    7       1.778    63.0 140.00000    5.24     6.55    800.00

============================================================================

Node Details

--------------

=============================================================================

Node    Peak Flow    Elevation    H G L    Cal Pres     Spc Pres   Meet Res

No.       (lps)        (m )        (m )      (m )         (m )    Pres. (Y)

-----------------------------------------------------------------------------

1 T       -1.778     128.00     141.66      13.66         8.00

2 T       -1.778      87.00     132.65      45.65         8.00

3 T       -1.778     118.00     126.00       8.00         8.00

Node Details  cont`d

---------------------

=============================================================================

Node    Peak Flow    Elevation    H G L    Cal Pres     Spc Pres   Meet Res

No.       (lps)        (m )        (m )      (m )         (m )    Pres. (Y)

-----------------------------------------------------------------------------

4 T       -1.778     105.00     116.87      11.87         8.00

5 T       -1.778     103.00     111.00       8.00         8.00

6 T       -1.778      61.00      86.34      25.34         8.00

7 T       -1.778      57.00      81.75      24.75         8.00

8          0.000     127.80     142.57      14.77         8.00

9          0.000      74.00     133.31      59.31         8.00

10          0.000     109.00     127.77      18.77         8.00

11          0.000     103.00     120.27      17.27         8.00

12          0.000     108.00     114.87       6.87 *       8.00

13          0.000      61.00      86.99      25.99         8.00

14 S       12.446     128.00     143.00      15.00         8.00

Cost Summary

--------------

=================================================

Diameter    Length        Cost        Cum. Cost

(mm)        (m )      (1000 Rs )    (1000 Rs )

-------------------------------------------------

63.0     3700.00        362.60        362.60

75.0      135.88         18.75        381.35

90.0      784.12        148.20        529.55

110.0      818.42        220.97        750.52

125.0     1181.58        410.01       1160.53

=================================================

Pipe-wise Cost Summary

------------------------

==========================================================

Pipe   Diameter      Length         Cost       Cum. Cost

No      (mm)        (m )       (1000 Rs )     (1000 Rs )

----------------------------------------------------------

1      125.0        50.00          17.35         17.35

2       63.0       140.00          13.72         31.07

3      110.0       168.42          45.47         76.54

125.0      1131.58         392.66        469.20

4       63.0       100.00           9.80        479.00

5      110.0       650.00         175.50        654.50

6       63.0       270.00          26.46        680.96

7       90.0       500.00          94.50        775.46

8       63.0       520.00          50.96        826.42

9       75.0       135.88          18.75        845.17

90.0       284.12          53.70        898.87

10       63.0      1180.00         115.64       1014.51

11       63.0       100.00           9.80       1024.31

12       63.0       590.00          57.82       1082.13

13       63.0       800.00          78.40       1160.53

ESR 19 – Kurung

| S.No. | village | Elevation |  | Population |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 2011 | 2026 | 2041 |
| 1 | Thakurwadi | 111 | 480 | 600 | 800 |
| 2 | Jambhulwadi | 106 | 480 | 600 | 800 |
| 3 | Haryachiwadi | 121 | 480 | 600 | 800 |
| 4 | Kurung | 96 | 650 | 765 | 899 |
|  | Total |  | 2090 | 2565 | 3299 |

| Daily Water Demand at 40 lpcd |
| --- |
| S.No. | village | Demand(MLD) | Demand(LPS) |
|  |  | 2011 | 2041 | 2011 | 2041 |
| 1 | Thakurwadi | 0.023 | 0.038 | 1.067 | 1.778 |
| 2 | Jambhulwadi | 0.023 | 0.038 | 1.067 | 1.778 |
| 3 | Haryachiwadi | 0.023 | 0.038 | 1.067 | 1.778 |
| 4 | Kurung | 0.031 | 0.043 | 1.444 | 1.999 |
|  | Total | 0.100 | 0.158 | 4.644 | 7.332 |

ESR 19 – Staging Height Optimization

| Total Demand | 158371 |  |  |  |
| --- | --- | --- | --- | --- |
| ESR capacity Required | 59389 |  |  |  |
| ESR capacity Proposed | 60000 |  |  |  |
| Low level Height | 130 |  |  |  |
| ESR elevation | 118 |  |  |  |
| HGL | PIPE cost | ESR cost | Total | height |
| 130 | 743.26 | 491.835 | 1235.095 | 12 |
| 131 | 735.59 | 501.6717 | 1237.262 | 13 |
| 132 | 729.92 | 511.5084 | 1241.428 | 14 |
| 133 | 720.25 | 521.3451 | 1241.595 | 15 |
| 134 | 712.58 | 531.1818 | 1243.762 | 16 |
| 135 | 704.91 | 545.9369 | 1250.847 | 17 |
| 136 | 697.24 | 560.6919 | 1257.932 | 18 |
| 137 | 689.57 | 575.447 | 1265.017 | 19 |
| 138 | 681.9 | 590.202 | 1272.102 | 20 |
| 139 | 674.22 | 609.8754 | 1284.095 | 21 |
| 140 | 666.55 | 629.5488 | 1296.099 | 22 |
| Optimum ESR height | 12 |  |  |  |
| ERS cost | 491.84 |  |  |  |
| Pipe cost | 743.26 |  |  |  |
| Total | 1235.10 |  |  |  |
| /person | 374 |  |  |  |

ESR 19 - BRANCH Input and Output

Echoing Input Variables

------------------------

Title of the Project                   :ESR 19(40 LPCD)

Name of the User                       :

Number of Pipes                        :  7

Number of Nodes                        :  8

Number of Commercial Diameters         :  16

Peak Design Factor                     :  1

Minimum Headloss in         m/km       :  .1

Maximum Headloss in         m/km       :  25

Minimum Residual Pressure   m          :  8

Type of Formula                        : Hazen's

Pipe Data

------------

===========================================================

Pipe  From   To     Length    Diameter  Hazen's   Status

No.  Node  Node      m         mm       Const    (E/P)

-----------------------------------------------------------

1     1     2       50.00

2     2     3      260.00

3     3     4      100.00

4     3     5      950.00

5     2     6     2450.00

6     6     7      770.00

7     7     8      470.00

===========================================================

Node Data

-----------

============================================================

Node   Peak      Flow     Elevation  Res. Press  Meet Res.

No.   Factor     lps         m           m      Pres (Y/N)?

------------------------------------------------------------

1   1.00       0.000      118.00       8.00

2   1.00       0.000      117.90       8.00

3   1.00       0.000      111.00       8.00

4   1.00      -1.778      111.00       8.00

5   1.00      -1.778      106.00       8.00

6   1.00       0.000       74.00       8.00

7   1.00      -1.778      121.00       8.00

8   1.00      -1.999       96.00       8.00

============================================================

Reference Node Data

---------------------

===================

Node   Grade Line

No.       m

-------------------

1      130.00

===================

Commercial Diameter Data

--------------------------

====================================

Pipe Dia.   Hazen's    Unit Cost

Int. (mm)   Const    Rs /m   length

------------------------------------

63.0   140.00000       98.00

75.0   140.00000      138.00

90.0   140.00000      189.00

110.0   140.00000      270.00

125.0   140.00000      347.00

140.0   140.00000      432.00

160.0   140.00000      556.00

180.0   140.00000      695.00

200.0   140.00000      789.00

225.0   140.00000     1004.00

250.0   140.00000     1228.00

280.0   140.00000     1532.00

315.0   140.00000     1932.00

355.0   140.00000     2210.00

400.0   140.00000     3147.00

500.0   140.00000     4000.00

====================================

Branched Water Distribution Network Design OutPut

---------------------------------------------------

Pipe Details

--------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

1    1    2       7.333    90.0 140.00000    0.79    15.80     50.00

2    2    3       3.556    63.0 140.00000    6.14    23.62    260.00

3    3    4       1.778    63.0 140.00000    0.66     6.60    100.00

Pipe Details  cont`d

---------------------

============================================================================

Pipe From  To   Peak Flow   Diam   Hazen's     HL    HL/1000  Length Status

No. Node Node    (lps)     (mm)    Const     (m )     (m )    (m )   (E/P)

----------------------------------------------------------------------------

4    3    5       1.778    63.0 140.00000    6.22     6.55    950.00

5    2    6       3.777    75.0 140.00000   10.90    11.30    964.63

90.0 140.00000    6.91     4.65   1485.37

6    6    7       3.777    90.0 140.00000    3.58     4.65    770.00

7    7    8       1.999    63.0 140.00000    3.82     8.13    470.00

============================================================================

Node Details

--------------

=============================================================================

Node    Peak Flow    Elevation    H G L    Cal Pres     Spc Pres   Meet Res

No.       (lps)        (m )        (m )      (m )         (m )    Pres. (Y)

-----------------------------------------------------------------------------

1 S        7.333     118.00     130.00      12.00         8.00

2          0.000     117.90     129.21      11.31         8.00

3          0.000     111.00     123.07      12.07         8.00

4 T       -1.778     111.00     122.41      11.41         8.00

5 T       -1.778     106.00     116.84      10.84         8.00

6          0.000      74.00     111.40      37.40         8.00

7         -1.778     121.00     107.82     -13.18 *       8.00

8 T       -1.999      96.00     104.00       8.00         8.00

=============================================================================

Cost Summary

--------------

=================================================

Diameter    Length        Cost        Cum. Cost

(mm)        (m )      (1000 Rs )    (1000 Rs )

-------------------------------------------------

63.0     1780.00        174.44        174.44

75.0      964.63        133.12        307.56

90.0     2305.37        435.72        743.27

=================================================

Pipe-wise Cost Summary

------------------------

==========================================================

Pipe   Diameter      Length         Cost       Cum. Cost

No      (mm)        (m )       (1000 Rs )     (1000 Rs )

----------------------------------------------------------

1       90.0        50.00           9.45          9.45

2       63.0       260.00          25.48         34.93

3       63.0       100.00           9.80         44.73

4       63.0       950.00          93.10        137.83

5       75.0       964.63         133.12        270.95

90.0      1485.37         280.73        551.68

6       90.0       770.00         145.53        697.21

7       63.0       470.00          46.06        743.27

Appendix 8.4.1

ESR Construction Cost Details

Appendix 8.4.2

DHPE Piping Cost Details

# Text boxes

ESR 2 - Pathraj

ESR 3 - Tadwadi

ESR 4 - Bangarwadi

ESR 5 - Khandas

ESR 6 - Mangalwadi

ESR 7 - Nandgaon

ESR 8 - Chai

ESR 9 - Bhopalwadi

ESR 10 Bondshet

ESR 11 Borgaon

ESR 12 - Aleman

ESR 13 - Murchulwadi

ESR 14 - Kalamb

ESR 15 - Salokh

ESR 16 - Male

ESR 17 - Vara

ESR 18 - Chinchpada

ESR 19 - Kurung

ESR 1 - Shilar

ESR 2 - Pathraj

ESR 3 - Tadwadi

ESR 4 - Bangarwadi

ESR 5 - Khandas

ESR 6 - Mangalwadi

ESR 7 - Nandgaon

ESR 8 - Chai

ESR 9 - Bhopalwadi

ESR 10 Bondshet

ESR 11 Borgaon

ESR 12 - Aleman

ESR 13 - Murchulwadi

ESR 14 - Kalamb

ESR 15 - Salokh

ESR 16 - Male

ESR 17 - Vara

ESR 18 - Chinchpada

ESR 19 - Kurung

ESR 1 - Shilar