## General
JalTantra: System For Optimization of Piped Water Networks, version:2.2.2.0
developed by CSE and CTARA departments of IIT Bombay
Mar 10, 2017 20:56 PM
Network Name |  |  | Sample
Organization Name |  |  | IIT Bombay
Minimum Node Pressure |  |  | 7
Default Pipe Roughness 'C' |  |  | 140
Minimum Headloss per KM |  |  | 0
Maximum Headloss per KM |  |  | 10
Maximum Water Speed
Maximum Pipe Pressure
Number of Supply Hours |  |  | 12
Source Node ID |  |  | 8
Source Node Name |  |  | Node8
Source Elevation |  |  | 505
Source Head |  |  | 530
Number of Nodes |  |  | 10
ESR Enabled |  |  | FALSE
Pump Enabled |  |  | FALSE
Total Length of Network |  |  | 35735
Total Length of New Pipes |  |  | 28390
Total Pipe Cost |  |  | 13048236.7058
NODE RESULTS
Node ID | Node Name | Demand | Elevation | Head | Pressure | Min. Pressure
1 | Node1 | 4.2 | 442 | 455.283 | 13.283 | 7
2 | Node2 | 1.6 | 477 | 491.1644 | 14.1644 | 7
3 | Node3 | 6.8 | 496 | 518.0274 | 22.0274 | 7
4 | Node4 | 3.5 | 464 | 480.0148 | 16.0148 | 7
6 | Node6 | 3.6 | 390 | 476.5761 | 86.5761 | 7
7 | Node7 | 5.2 | 493 | 502.4939 | 9.4939 | 7
9 | Node9 | 0 | 517 | 524 | 7 | 7
10 | Node10 | 0 | 509 | 516 | 7 | 7
11 | Node11 | 0 | 472 | 479 | 7 | 7
PIPE RESULTS
Pipe ID | Start Node | End Node | Length | Flow | Speed | Diameter | Roughness 'C' | Headloss | Headloss per KM | Cost | Pump Head | Pump Power | Valve Setting | Status
2 | 3 | 7 | 7345 | 4.2244 | 0.44452 | 110 | 140 | 15.5335 | 2.1148 | 0
|  |  | 7345 | 0.97559 | 0.31297 | 63 | 140 | 15.5335 | 2.1148 | 852020 |  |  |  | Parallel
3 | 2 | 6 | 3491 | 3.6 | 0.56588 | 90 | 140 | 14.5882 | 4.1788 | 806421
4 | 2 | 4 | 914.8501 | 7.7 | 0.81024 | 110 | 140 | 5.8815 | 6.429 | 311049.0272
4 | 2 | 4 | 1527.1499 | 7.7 | 0.62745 | 125 | 140 | 5.2681 | 3.4496 | 704016.1131
5 | 9 | 3 | 1943 | 24.9 | 0.79259 | 200 | 140 | 5.9726 | 3.0739 | 2162559
6 | 8 | 9 | 1004.3129 | 24.9 | 0.79259 | 200 | 140 | 3.0871 | 3.0739 | 1117800.28
6 | 8 | 9 | 1681.6871 | 24.9 | 0.62625 | 225 | 140 | 2.9129 | 1.7321 | 2404812.5244
7 | 10 | 2 | 4808 | 12.9 | 0.838 | 140 | 140 | 24.8356 | 5.1655 | 2769408
8 | 3 | 10 | 530.1294 | 12.9 | 0.64159 | 160 | 140 | 1.4291 | 2.6958 | 397597.0725
8 | 3 | 10 | 393.8706 | 12.9 | 0.50694 | 180 | 140 | 0.59832 | 1.5191 | 372207.6887
9 | 11 | 1 | 4266 | 4.2 | 0.6602 | 90 | 140 | 23.717 | 5.5595 | 985446
10 | 4 | 11 | 485 | 4.2 | 0.44195 | 110 | 140 | 1.0148 | 2.0923 | 164900
COST RESULTS OF NEW PIPES
Diameter | Length | Cost | Cumulative Cost
63 | 7345 | 852020 | 852020
90 | 7757 | 1791867 | 2643887
110 | 1399.8501 | 475949.0272 | 3119836.0272
125 | 1527.1499 | 704016.1131 | 3823852.1403
140 | 4808 | 2769408 | 6593260.1403
160 | 530.1294 | 397597.0725 | 6990857.2128
180 | 393.8706 | 372207.6887 | 7363064.9015
200 | 2947.3129 | 3280359.28 | 10643424.1814
225 | 1681.6871 | 2404812.5244 | 13048236.7058
Total | 28390 | 13048236.7058